## Table 1
Module Number: AR3S1L3M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.8997 | 6.5949 | 183.9965 | 35.3954 | 8.7613 | Hotspot formed over the cells or burned cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.2956 | 4.8716 | 123.2299 | 32.6422 | 6.5294
Difference | 1.1003 | 0.8251 | 31.0035 | 0.6046 | -0.4613
Percentage Degradation | 3.7941 | 11.1196 | 14.4202 | 1.6795 | -5.558
Module Number: AR3S1L2U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.6472 | 6.158 | 176.4086 | 35.4203 | 7.5194 | Cell performance is degraded or snail trails are formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.7727 | 4.628 | 119.2764 | 32.4585 | 5.7052
Difference | 0.3528 | 1.262 | 38.5914 | 0.5797 | 0.7806
Percentage Degradation | 1.2164 | 17.0086 | 17.9495 | 1.6103 | 9.4052

## Table 2
Module Number: AR3S3L2L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 29.6611 | 5.9978 | 177.9012 | 35.4714 | 7.5775 | Hotspot formed over the cells or burned cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 26.9759 | 4.5927 | 123.8912 | 32.7953 | 5.8523
Difference | -0.6611 | 1.4222 | 37.0988 | 0.5286 | 0.7225
Percentage Degradation | -2.2797 | 19.1672 | 17.2553 | 1.4684 | 8.7052
Module Number: AR3S7L2M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.7577 | 6.3521 | 176.3188 | 34.4413 | 7.7795 | Hotspot formed over the cells or cell performance is degraded or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 26.1659 | 5.2877 | 138.3571 | 32.7953 | 6.5113
Difference | 1.2423 | 1.0679 | 38.6812 | 1.5587 | 0.5205
Percentage Degradation | 4.2837 | 14.3927 | 17.9913 | 4.3298 | 6.2715

## Table 3
Module Number: AR3S8L1M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.1257 | 5.1569 | 139.8838 | 34.4621 | 7.4032 | Cell performance is degraded or hotspot are formed over the cells or cell burn or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.4935 | 4.3032 | 109.7031 | 32.7341 | 6.213
Difference | 1.8743 | 2.2631 | 75.1162 | 1.5379 | 0.8968
Percentage Degradation | 6.4631 | 30.5003 | 34.9378 | 4.2719 | 10.805
Module Number: AR3S10L1L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 29.6404 | 6.395 | 189.5509 | 35.4626 | 8.6894 | Hotspot formed over the cells or burned cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 26.9345 | 4.883 | 131.5213 | 32.7647 | 6.6927
Difference | -0.6404 | 1.025 | 25.4491 | 0.5374 | -0.3894
Percentage Degradation | -2.2083 | 13.8138 | 11.8368 | 1.4927 | -4.6921

## Table 4
Module Number: AR3S10L3M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.9213 | 6.3483 | 183.5998 | 35.4762 | 7.7144 | Cell performance is degraded or hotspot are formed over the cells or cell burn or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 26.0291 | 4.8969 | 127.4627 | 32.5198 | 6.0075
Difference | 0.0787 | 1.0717 | 31.4002 | 0.5238 | 0.5856
Percentage Degradation | 0.2713 | 14.444 | 14.6047 | 1.4549 | 7.055
Module Number: AR3S10L4M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 29.2027 | 6.3051 | 184.1266 | 35.5039 | 7.559 | Cell performance is degraded or hotspot are formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 26.5292 | 4.9093 | 130.2405 | 32.7953 | 5.9369
Difference | -0.2027 | 1.1149 | 30.8734 | 0.4961 | 0.741
Percentage Degradation | -0.6989 | 15.0252 | 14.3597 | 1.378 | 8.9277

## Table 5
Module Number: AR3S11L3M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.1383 | 5.7971 | 157.3239 | 35.1952 | 7.4765 | Cell performance is degraded or hotspot are formed over the cells or low fill factor or increased series resistance of the cells or snail trails are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.6628 | 4.5776 | 112.8973 | 32.5198 | 5.9551
Difference | 1.8617 | 1.6229 | 57.6761 | 0.8048 | 0.8235
Percentage Degradation | 6.4195 | 21.8718 | 26.8261 | 2.2356 | 9.9213
Module Number: AR3S11L4L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.5183 | 5.5431 | 146.9941 | 34.2934 | 7.211 | Cell performance is degraded or hotspot are formed over the cells or low fill factor or snail trails are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.6736 | 4.7322 | 116.7613 | 32.3054 | 6.1969
Difference | 2.4817 | 1.8769 | 68.0059 | 1.7066 | 1.089
Percentage Degradation | 8.5576 | 25.2949 | 31.6307 | 4.7405 | 13.1209

## Table 6
Module Number: AR4S8L3L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 16.9214 | 7.4884 | 126.7148 | 23.2856 | 8.2944 | One of the sub-string is open circuited or cells in sub-string burned or faulty bypass diode or snail trails formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 15.6013 | 6.2885 | 98.109 | 21.7717 | 7.0171
Difference | 12.0786 | -0.0684 | 88.2852 | 12.7144 | 0.0056
Percentage Degradation | 41.6502 | -0.9221 | 41.0629 | 35.3178 | 0.0676
Module Number: AR4S8L1M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 16.1373 | 7.5475 | 121.7966 | 22.903 | 8.4384 | One of the sub-string is open circuited or cells in sub-string burned or faulty bypass diode or snail trails formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 15.0254 | 6.4592 | 97.0525 | 21.588 | 7.269
Difference | 12.8627 | -0.1275 | 93.2034 | 13.097 | -0.1384
Percentage Degradation | 44.3543 | -1.7189 | 43.3504 | 36.3807 | -1.6675

## Table 7
Module Number: AR5S1L3M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 25.6651 | 7.5407 | 193.5319 | 35.6265 | 8.6181 | Series resistance of module increases or low fill factor or snail trails formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 23.1118 | 6.2569 | 144.6073 | 32.6729 | 7.2186
Difference | 3.3349 | -0.1207 | 21.4681 | 0.3735 | -0.3181
Percentage Degradation | 11.4995 | -1.626 | 9.9852 | 1.0375 | -3.8325
Module Number: AR5S2L2L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 24.6898 | 7.2987 | 180.2031 | 34.7739 | 8.3446 | Series resistance of module increases or low fill factor or snail trails formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 22.6649 | 6.0428 | 136.9591 | 32.3973 | 6.9627
Difference | 4.3102 | 0.1213 | 34.7969 | 1.2261 | -0.0446
Percentage Degradation | 14.8628 | 1.6349 | 16.1846 | 3.4059 | -0.5375

## Table 8
Module Number: AR5S5L1L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 15.196 | 7.3826 | 112.1862 | 35.62 | 8.2209 | Hotspot formed over the cells or burned cells or low fill factor or snail trails are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 13.6716 | 6.1075 | 83.4985 | 32.6422 | 6.866
Difference | 13.804 | 0.0374 | 102.8138 | 0.38 | 0.0791
Percentage Degradation | 47.6001 | 0.5037 | 47.8204 | 1.0556 | 0.9525
Module Number: AR5S5L2M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 14.9823 | 6.8926 | 103.2664 | 23.4437 | 8.505 | One of the sub-string is open circuited or cells in sub-string burned or faulty bypass diode or snail trails formed over the cells or bubbles are form at the backsheet of module.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 13.7235 | 5.7113 | 78.3794 | 21.8023 | 7.1038
Difference | 14.0177 | 0.5274 | 111.7336 | 12.5563 | -0.205
Percentage Degradation | 48.3371 | 7.1081 | 51.9691 | 34.8786 | -2.4694

## Table 9
Module Number: AR5S6L4L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.3555 | 7.1336 | 188.0096 | 34.7094 | 7.892 | Hotspot formed over the cells or low fill factor or snail trails are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.4161 | 6.4307 | 157.0126 | 32.581 | 7.1642
Difference | 2.6445 | 0.2864 | 26.9904 | 1.2906 | 0.408
Percentage Degradation | 9.119 | 3.8599 | 12.5537 | 3.585 | 4.9158
Module Number: AR5S8L1L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.2952 | 6.1006 | 172.6171 | 35.6691 | 6.7046 | Cell performance is degraded or hotspot are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.239 | 5.485 | 138.4362 | 32.4585 | 6.0901
Difference | 0.7048 | 1.3194 | 42.3829 | 0.3309 | 1.5954
Percentage Degradation | 2.4303 | 17.782 | 19.713 | 0.9191 | 19.2219

## Table 10
Module Number: AR5S8L2L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.6841 | 5.6332 | 161.5826 | 35.7917 | 7.3085 | Cell performance is degraded or hotspot are formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.5375 | 5.0851 | 129.8618 | 32.5198 | 6.6665
Difference | 0.3159 | 1.7868 | 53.4174 | 0.2083 | 0.9915
Percentage Degradation | 1.0893 | 24.0812 | 24.8453 | 0.5786 | 11.9453
Module Number: AR5S8L3L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 17.7023 | 4.1077 | 72.7161 | 33.3665 | 6.4406 | Cell performance is degraded or hotspot are formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 16.1689 | 3.7326 | 60.3514 | 30.9581 | 5.9007
Difference | 11.2977 | 3.3123 | 142.2839 | 2.6335 | 1.8594
Percentage Degradation | 38.9577 | 44.6398 | 66.1785 | 7.3153 | 22.4021

## Table 11
Module Number: AR6S11L4L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.9142 | 6.1773 | 172.4343 | 35.3797 | 6.7877 | Cell performance is degraded or hotspot are formed over the cells or snail trails are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.0035 | 5.7095 | 142.7566 | 32.3054 | 6.336
Difference | 1.0858 | 1.2427 | 42.5657 | 0.6203 | 1.5123
Percentage Degradation | 3.7443 | 16.7479 | 19.798 | 1.7232 | 18.2203
Module Number: AR6S7L1M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.1493 | 6.2209 | 168.8932 | 34.403 | 6.7141 | Cell performance is degraded or hotspot are formed over the cells or light temp variation within module backsheet.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.9889 | 5.3093 | 132.6742 | 32.1217 | 5.7737
Difference | 1.8507 | 1.1991 | 46.1068 | 1.597 | 1.5859
Percentage Degradation | 6.3818 | 16.1602 | 21.445 | 4.436 | 19.107

## Table 12
Module Number: AR6S6L3M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.7193 | 6.3933 | 183.6108 | 35.4987 | 7.5294 | Cell performance is degraded or hotspot are formed over the cells or burned cell.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.8867 | 5.5604 | 143.9406 | 32.581 | 6.61
Difference | 0.2807 | 1.0267 | 31.3892 | 0.5013 | 0.7706
Percentage Degradation | 0.9679 | 13.8371 | 14.5996 | 1.3926 | 9.2842
Module Number: AR6S4L1L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.6008 | 5.4815 | 151.2942 | 34.5214 | 7.4101 | Cell performance is degraded or hotspot are formed over the cells or burned cell.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.7391 | 4.8629 | 125.1659 | 32.581 | 6.6161
Difference | 1.3992 | 1.9385 | 63.7058 | 1.4786 | 0.8899
Percentage Degradation | 4.8247 | 26.1252 | 29.6306 | 4.1071 | 10.7212

## Table 13
Module Number: AR7S2L3L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 16.7366 | 4.8122 | 80.5406 | 33.364 | 6.8901 | Cell performance is degraded or hotspot are formed over the cells or low fill factor or snail trails are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 15.4726 | 4.2916 | 66.4025 | 31.2643 | 6.1888
Difference | 12.2634 | 2.6078 | 134.4594 | 2.636 | 1.4099
Percentage Degradation | 42.2876 | 35.1449 | 62.5393 | 7.3222 | 16.9869
Module Number: AR8S1L2L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 29.2158 | 4.9912 | 145.8219 | 34.9056 | 7.3807 | Cell performance is degraded or hotspot are formed over the cells or low fill factor or burned cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 26.6965 | 4.4742 | 119.4446 | 32.3973 | 6.6705
Difference | -0.2158 | 2.4288 | 69.1781 | 1.0944 | 0.9193
Percentage Degradation | -0.7443 | 32.7333 | 32.1759 | 3.0401 | 11.0758

## Table 14
Module Number: AR8S1L3L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.1115 | 6.3404 | 178.2374 | 35.3371 | 7.595 | Cell performance is degraded or hotspot are formed over the cells or low fill factor or burned cell.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.4512 | 5.6905 | 144.8312 | 32.5504 | 6.8781
Difference | 0.8885 | 1.0796 | 36.7626 | 0.6629 | 0.705
Percentage Degradation | 3.0637 | 14.5503 | 17.0989 | 1.8413 | 8.4936
Module Number: AR8S1L4L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.3649 | 6.2759 | 171.7408 | 34.8167 | 6.9864 | Cell performance is degraded or hotspot are formed over the cells or snail trails are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.9386 | 5.6314 | 140.4405 | 32.2442 | 6.3218
Difference | 1.6351 | 1.1441 | 43.2592 | 1.1833 | 1.3136
Percentage Degradation | 5.6382 | 15.4185 | 20.1205 | 3.2869 | 15.827

## Table 15
Module Number: AR8S1L4M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.558 | 5.9111 | 162.8979 | 34.791 | 7.2693 | Cell performance is degraded or hotspot are formed over the cells or snail trails are formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.1371 | 5.3239 | 133.8279 | 32.2442 | 6.602
Difference | 1.442 | 1.5089 | 52.1021 | 1.209 | 1.0307
Percentage Degradation | 4.9726 | 20.3355 | 24.2335 | 3.3584 | 12.4181
Module Number: AR8S3L2L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.7779 | 6.6141 | 183.7265 | 35.5438 | 7.2652 | Cell performance is degraded or snail trails are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.9132 | 5.9318 | 147.781 | 32.4891 | 6.5798
Difference | 1.2221 | 0.8059 | 31.2735 | 0.4562 | 1.0348
Percentage Degradation | 4.2141 | 10.8609 | 14.5458 | 1.2672 | 12.4669

## Table 16
Module Number: AR8S3L3L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.6762 | 6.4256 | 171.4105 | 34.6118 | 7.0162 | Cell performance is degraded or snail trails are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.4865 | 5.7502 | 140.8032 | 32.2442 | 6.3279
Difference | 2.3238 | 0.9944 | 43.5895 | 1.3882 | 1.2838
Percentage Degradation | 8.013 | 13.4018 | 20.2742 | 3.8562 | 15.467
Module Number: AR8S3L4L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.1709 | 6.3039 | 164.98 | 34.4765 | 6.9507 | Cell performance is degraded or snail trails are formed over the cells or hotspot formed on cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.1095 | 5.6674 | 136.6377 | 32.2135 | 6.2956
Difference | 2.8291 | 1.1161 | 50.02 | 1.5235 | 1.3493
Percentage Degradation | 9.7555 | 15.0411 | 23.2651 | 4.2319 | 16.2572

## Table 17
Module Number: AR8S6L2L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 17.901 | 6.5761 | 117.7186 | 24.8978 | 6.8654 | Cell performance is degraded or one of the sub-string is open circuited or cells in sub- string burned or faulty bypass diode or snail trails are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 16.1021 | 6.0478 | 97.3819 | 22.8128 | 6.3742
Difference | 11.099 | 0.8439 | 97.2814 | 11.1022 | 1.4346
Percentage Degradation | 38.2725 | 11.3734 | 45.2472 | 30.8394 | 17.2847
Module Number: AR8S6L4U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 24.6993 | 6.8856 | 170.0693 | 35.8177 | 8.1337 | Increased series resistance of module or hotspot formed over the cells or snail trails are formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 21.8182 | 6.302 | 137.4978 | 32.336 | 7.527
Difference | 4.3007 | 0.5344 | 44.9307 | 0.1823 | 0.1663
Percentage Degradation | 14.83 | 7.2023 | 20.898 | 0.5065 | 2.0039

## Table 18
Module Number: AR8S8L4M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.9641 | 6.1359 | 177.7211 | 35.805 | 7.8576 | Cell performance is degraded or hotspot formed over the cells or snail trails are formed over the cells or low fill factor or burned cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.6858 | 5.5784 | 143.2857 | 32.4279 | 7.2206
Difference | 0.0359 | 1.2841 | 37.2789 | 0.195 | 0.4424
Percentage Degradation | 0.1239 | 17.3058 | 17.339 | 0.5416 | 5.3303
Module Number: AR8S10L1L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 25.9675 | 6.6059 | 171.5395 | 34.0036 | 7.0495 | Cell performance is degraded or temperature variation within the cells of module or snail trails are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.0184 | 6.2289 | 149.6088 | 31.8767 | 6.6947
Difference | 3.0325 | 0.8141 | 43.4605 | 1.9964 | 1.2505
Percentage Degradation | 10.4568 | 10.9714 | 20.2142 | 5.5455 | 15.0667

## Table 19
Module Number: AR8S10L3U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 24.4957 | 6.9896 | 171.216 | 34.3583 | 7.9005 | Increased series resistance of module or hotspot formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 22.5559 | 6.5421 | 147.5632 | 32.0911 | 7.4504
Difference | 4.5043 | 0.4304 | 43.784 | 1.6417 | 0.3995
Percentage Degradation | 15.5321 | 5.8 | 20.3647 | 4.5602 | 4.8135
Module Number: AR8S10L4L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 24.8834 | 6.6012 | 164.2601 | 34.298 | 7.4055 | Cell performance is degraded or Increased series resistance of module or low fill factor or temperature variation within the cells of module at backsheet.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 22.7221 | 6.1681 | 140.1512 | 31.8155 | 6.9768
Difference | 4.1166 | 0.8188 | 50.7399 | 1.702 | 0.8945
Percentage Degradation | 14.1951 | 11.0352 | 23.5999 | 4.7278 | 10.7776

## Table 20
Module Number: AR8S11L1U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.2117 | 6.5513 | 178.2733 | 35.3769 | 7.0372 | Cell performance is degraded or snail trails are formed over the cells or hotspot formed on the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.3483 | 6.1632 | 150.0636 | 32.2748 | 6.6866
Difference | 1.7883 | 0.8687 | 36.7267 | 0.6231 | 1.2628
Percentage Degradation | 6.1665 | 11.707 | 17.0822 | 1.7307 | 15.2147
Module Number: AR8S12L4U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 24.8573 | 4.9923 | 124.0953 | 35.413 | 7.7505 | Cell performance is degraded or snail trails are formed over the cells or hotspot formed on the cells or burned cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 22.3429 | 4.6787 | 104.5345 | 32.4279 | 7.3335
Difference | 4.1427 | 2.4277 | 90.9047 | 0.587 | 0.5495
Percentage Degradation | 14.2852 | 32.7183 | 42.2813 | 1.6304 | 6.6209

## Table 21
Module Number: AR9S11L3M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 22.3029 | 5.63 | 125.5665 | 33.6543 | 7.5885 | Cell performance is degraded or snail trails are formed over the cells or hotspot formed on the cells or temperature variation within the cells of module at backsheet or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 20.2561 | 5.2944 | 107.2446 | 31.0806 | 7.1985
Difference | 6.6971 | 1.79 | 89.4335 | 2.3457 | 0.7115
Percentage Degradation | 23.0933 | 24.1234 | 41.597 | 6.5157 | 8.5726
Module Number: AR9S4L1L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 22.6554 | 6.2079 | 140.6433 | 33.4604 | 7.4499 | Cell performance is degraded or snail trails are formed over the cells or hotspot formed on the cells or temperature variation within the cells of module at backsheet or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 20.7964 | 5.6353 | 117.1943 | 31.1724 | 6.8156
Difference | 6.3446 | 1.2121 | 74.3567 | 2.5396 | 0.8501
Percentage Degradation | 21.8779 | 16.3352 | 34.5845 | 7.0544 | 10.2419

## Table 22
Module Number: AR10S1L4L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.7344 | 5.7684 | 154.2139 | 34.7743 | 6.9481 | Cell performance is degraded or hotspot formed on the cells or burned cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.4284 | 5.2372 | 127.9374 | 32.2748 | 6.3601
Difference | 2.2656 | 1.6516 | 60.7861 | 1.2257 | 1.3519
Percentage Degradation | 7.8124 | 22.2591 | 28.2726 | 3.4047 | 16.2882
Module Number: AR11S6L4L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 25.696 | 5.9923 | 153.9771 | 33.3908 | 7.8637 | Cell performance is degraded or hotspot formed on the cells or burned cells or low fill factor or temperature variation within the cells of module at backsheet or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 23.3646 | 5.3485 | 124.9669 | 30.8662 | 7.0796
Difference | 3.304 | 1.4277 | 61.0229 | 2.6092 | 0.4363
Percentage Degradation | 11.3932 | 19.2417 | 28.3828 | 7.2479 | 5.2569

## Table 23
Module Number: AR11S7L2L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.4717 | 5.8349 | 160.2952 | 34.6266 | 7.0085 | Cell performance is degraded or hotspot formed on the cells or burned cells or low fill factor or snail trails are formed on the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.1161 | 5.3138 | 133.4614 | 32.1523 | 6.4347
Difference | 1.5283 | 1.5851 | 54.7048 | 1.3734 | 1.2915
Percentage Degradation | 5.2698 | 21.3624 | 25.4441 | 3.8149 | 15.56
Module Number: AR11S8L4U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 18.8516 | 4.4452 | 83.7987 | 33.8513 | 7.0305 | Cell performance is degraded or hotspot formed on the cells or burned cells or low fill factor or temperature variation within the cells of module at backsheet or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 17.1432 | 4.232 | 72.5496 | 31.2949 | 6.7511
Difference | 10.1484 | 2.9748 | 131.2013 | 2.1487 | 1.2695
Percentage Degradation | 34.9946 | 40.0919 | 61.0239 | 5.9687 | 15.2946

## Table 24
Module Number: AR11S9L3M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 22.0694 | 4.24 | 93.5752 | 33.3993 | 7.0097 | Cell performance is degraded or burned cells or low fill factor or snail trails are formed on the cells or temperature variation within the cells of module at backsheet or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 20.1094 | 3.978 | 79.9959 | 30.9274 | 6.6322
Difference | 6.9306 | 3.18 | 121.4248 | 2.6007 | 1.2903
Percentage Degradation | 23.8986 | 42.8566 | 56.4767 | 7.2241 | 15.5457
Module Number: AR11S10L1M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 14.0327 | 6.409 | 89.9357 | 35.8868 | 7.9726 | Cells in the sub- strings are burned or one the end of sub-strings is open circuited or fauty diode or snail trails are formed on cells or snail trails are formed on the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 12.4959 | 6.0621 | 75.7513 | 32.6116 | 7.6197
Difference | 14.9673 | 1.011 | 125.0643 | 0.1132 | 0.3274
Percentage Degradation | 51.6114 | 13.6251 | 58.1694 | 0.3145 | 3.9451

## Table 25
Module Number: AR12S11L3L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 23.6764 | 6.1062 | 144.5715 | 33.7725 | 6.8388 | Cell performance is degraded or increased series resistance of the module or low fill factor or snail trails are formed on the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 21.6178 | 5.7321 | 123.9144 | 31.3255 | 6.473
Difference | 5.3236 | 1.3138 | 70.4285 | 2.2275 | 1.4612
Percentage Degradation | 18.3573 | 17.7069 | 32.7574 | 6.1875 | 17.6046
Module Number: AR12S11L1U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 24.1046 | 6.6847 | 161.1309 | 35.8863 | 8.1316 | Increased series resistance of the module or low fill factor or snail trails are formed on the cells or hotspot formed on the module.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 21.8846 | 6.3111 | 138.1171 | 33.1322 | 7.7446
Difference | 4.8954 | 0.7353 | 53.8691 | 0.1137 | 0.1684
Percentage Degradation | 16.8808 | 9.9102 | 25.0554 | 0.3157 | 2.0284

## Table 26
Module Number: AR12S10L1L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.9576 | 6.4971 | 175.1464 | 35.8816 | 7.4522 | Cell performance is degraded or low fill factor or snail trails are formed on the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.0924 | 6.1278 | 147.6329 | 32.7035 | 7.0997
Difference | 2.0424 | 0.9229 | 39.8536 | 0.1184 | 0.8478
Percentage Degradation | 7.0426 | 12.438 | 18.5366 | 0.329 | 10.2144
Module Number: AR13S2L3L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 19.1931 | 5.0215 | 96.3783 | 32.9764 | 6.6284 | Cell performance is degraded or burned cells or low fill factor or snail trails are formed on the cells or hotspot formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 17.7621 | 4.6767 | 83.068 | 30.9274 | 6.2171
Difference | 9.8069 | 2.3985 | 118.6217 | 3.0236 | 1.6716
Percentage Degradation | 33.8167 | 32.3249 | 55.1729 | 8.399 | 20.1403

## Table 27
Module Number: AR13S2L3M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 18.7313 | 4.9013 | 91.8073 | 33.3387 | 6.9696 | Cell performance is degraded or burned cells or low fill factor or snail trails are formed on the cells or hotspot formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 17.2501 | 4.5644 | 78.7368 | 31.1418 | 6.5395
Difference | 10.2687 | 2.5187 | 123.1927 | 2.6613 | 1.3304
Percentage Degradation | 35.4093 | 33.9451 | 57.2989 | 7.3925 | 16.0287
Module Number: AR14S3L3L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.635 | 5.7446 | 158.753 | 34.3888 | 6.3491 | Cell performance is degraded or low fill factor or snail trails are formed on the cells or hotspot formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.4487 | 5.3659 | 136.5561 | 32.1217 | 5.9752
Difference | 1.365 | 1.6754 | 56.247 | 1.6112 | 1.9509
Percentage Degradation | 4.707 | 22.5789 | 26.1614 | 4.4755 | 23.505

## Table 28
Module Number: AR14S4L1M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.7926 | 5.2668 | 146.3771 | 34.2724 | 6.8263 | Cell performance is degraded or burned cells or low fill factor or snail trails are formed on the cells or bubles are formed at the backsheet of module.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.6699 | 4.9411 | 126.8376 | 32.0911 | 6.4508
Difference | 1.2074 | 2.1532 | 68.6229 | 1.7276 | 1.4737
Percentage Degradation | 4.1636 | 29.0192 | 31.9176 | 4.7989 | 17.7551
Module Number: AR14S12L3M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 29.1014 | 5.9777 | 173.9606 | 35.8488 | 7.1524 | Cell performance is degraded or burned cells or low fill factor or snail trails are formed on the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.8882 | 5.5503 | 143.6872 | 32.5504 | 6.7108
Difference | -0.1014 | 1.4423 | 41.0394 | 0.1512 | 1.1476
Percentage Degradation | -0.3495 | 19.4373 | 19.0881 | 0.4199 | 13.8264

## Table 29
Module Number: AR15S12L2U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 19.8137 | 4.6459 | 92.0531 | 34.1652 | 7.1318 | Cell performance is degraded or burned cells or low fill factor or snail trails are formed on the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 17.9867 | 4.2972 | 77.2915 | 31.5399 | 6.6544
Difference | 9.1863 | 2.7741 | 122.9469 | 1.8348 | 1.1682
Percentage Degradation | 31.6768 | 37.3864 | 57.1846 | 5.0966 | 14.0744
Module Number: AR15S12L4M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.2047 | 6.2798 | 164.5594 | 35.8792 | 7.1935 | Cell performance is degraded or burned cells or low fill factor or hotspot formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 23.3678 | 5.917 | 138.266 | 32.6422 | 6.8478
Difference | 2.7953 | 1.1402 | 50.4406 | 0.1208 | 1.1065
Percentage Degradation | 9.6389 | 15.3672 | 23.4608 | 0.3356 | 13.3309

## Table 30
Module Number: AR16S7L2M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 25.1148 | 6.8315 | 171.5714 | 35.844 | 8.1175 | Increased series resistance of the module or low fill factor or snail trails are formed on the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 22.6544 | 6.318 | 143.1299 | 32.9178 | 7.5773
Difference | 3.8852 | 0.5885 | 43.4286 | 0.156 | 0.1825
Percentage Degradation | 13.3974 | 7.9313 | 20.1994 | 0.4333 | 2.1988
Module Number: AR16S6L3U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.7364 | 5.4371 | 150.8066 | 35.8307 | 7.8907 | Burned cells or hotspot formed over the cells or snail trails are formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.9737 | 4.9961 | 124.771 | 32.8566 | 7.3194
Difference | 1.2636 | 1.9829 | 64.1934 | 0.1693 | 0.4093
Percentage Degradation | 4.3574 | 26.7231 | 29.8574 | 0.4703 | 4.9316

## Table 31
Module Number: AR16S1L3L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.338 | 5.7646 | 163.3559 | 34.6944 | 7.0391 | Cell performance is degraded or burned cells or low fill factor or snail trails are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.9965 | 5.4692 | 142.179 | 32.3054 | 6.7309
Difference | 0.662 | 1.6554 | 51.6441 | 1.3056 | 1.2609
Percentage Degradation | 2.2828 | 22.3106 | 24.0205 | 3.6268 | 15.1918
Module Number: AR19S1L2M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.2412 | 6.0404 | 164.5485 | 34.8065 | 7.3453 | Cell performance is degraded or burned cells or low fill factor or hotspot formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.1223 | 5.7841 | 145.3089 | 32.5504 | 7.0856
Difference | 1.7588 | 1.3796 | 50.4515 | 1.1935 | 0.9547
Percentage Degradation | 6.0648 | 18.5926 | 23.4658 | 3.3153 | 11.5028

## Table 32
Module Number: AR19S1L2L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.2576 | 6.3056 | 171.8766 | 34.9934 | 7.1259 | Cell performance is degraded or burned cells or low fill factor or snail trails are formed over the cells or burned cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.0314 | 6.0853 | 152.3238 | 32.6116 | 6.9305
Difference | 1.7424 | 1.1144 | 43.1234 | 1.0066 | 1.1741
Percentage Degradation | 6.0082 | 15.0184 | 20.0574 | 2.7962 | 14.1454
Module Number: AR19S1L3U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.4392 | 6.2984 | 172.8241 | 35.0809 | 7.3157 | Cell performance is degraded or burned cells or low fill factor or hotspot formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.2652 | 6.096 | 154.0161 | 32.7647 | 7.134
Difference | 1.5608 | 1.1216 | 42.1759 | 0.9191 | 0.9843
Percentage Degradation | 5.3822 | 15.1153 | 19.6167 | 2.553 | 11.8587

## Table 33
Module Number: AR19S2L1M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.1935 | 4.948 | 139.501 | 35.174 | 7.3516 | Cell performance is degraded or burned cells or low fill factor or hotspot formed over the cells or snail trails are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.6994 | 4.7358 | 121.7077 | 32.581 | 7.0957
Difference | 0.8065 | 2.472 | 75.499 | 0.826 | 0.9484
Percentage Degradation | 2.7812 | 33.3155 | 35.1158 | 2.2944 | 11.426
Module Number: AR19S3L3L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.9387 | 5.6735 | 158.5109 | 34.5479 | 7.0822 | Cell performance is degraded or burned cells or low fill factor or hotspot formed over the cells or snail trails are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.8814 | 5.4011 | 139.7874 | 32.4279 | 6.7894
Difference | 1.0613 | 1.7465 | 56.4891 | 1.4521 | 1.2178
Percentage Degradation | 3.6597 | 23.5374 | 26.274 | 4.0337 | 14.6724

## Table 34
Module Number: AR19S4L1M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.3881 | 6.445 | 170.0701 | 34.8144 | 6.9541 | Cell performance is degraded or hotspot formed over the cells or snail trails are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.3567 | 6.1371 | 149.4793 | 32.581 | 6.6705
Difference | 2.6119 | 0.975 | 44.9299 | 1.1856 | 1.3459
Percentage Degradation | 9.0066 | 13.1408 | 20.8976 | 3.2934 | 16.2154
Module Number: AR19S4L2L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.1365 | 5.3577 | 145.3885 | 34.9122 | 7.6494 | Cell performance is degraded or burned cells or low fill factor or hotspot formed over the cells or snail trails are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.8479 | 5.0717 | 126.0202 | 32.4585 | 7.2992
Difference | 1.8635 | 2.0623 | 69.6115 | 1.0878 | 0.6506
Percentage Degradation | 6.4258 | 27.7942 | 32.3774 | 3.0217 | 7.8384

## Table 35
Module Number: AR19S4L3U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.0893 | 5.9421 | 166.9091 | 34.556 | 7.2953 | Cell performance is degraded or burned cells or low fill factor or hotspot formed over the cells or snail trails are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.6252 | 5.5933 | 143.3284 | 32.0298 | 6.9244
Difference | 0.9107 | 1.4779 | 48.0909 | 1.444 | 1.0047
Percentage Degradation | 3.1402 | 19.918 | 22.3678 | 4.0112 | 12.1048
Module Number: AR19S5L4M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.9555 | 5.9744 | 161.042 | 35.7535 | 7.1631 | Cell performance is degraded or burned cells or low fill factor or hotspot formed over the cells or snail trails are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.0022 | 5.6142 | 134.7532 | 32.4891 | 6.8015
Difference | 2.0445 | 1.4456 | 53.958 | 0.2465 | 1.1369
Percentage Degradation | 7.0501 | 19.4828 | 25.0967 | 0.6848 | 13.698

## Table 36
Module Number: AR19S6L2L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.056 | 6.1239 | 165.689 | 34.493 | 6.9281 | Cell performance is degraded or hotspot formed over the cells or snail trails are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.8816 | 5.7666 | 143.4817 | 32.1829 | 6.5738
Difference | 1.944 | 1.2961 | 49.311 | 1.507 | 1.3719
Percentage Degradation | 6.7033 | 17.4674 | 22.9353 | 4.186 | 16.5292
Module Number: AR19S6L3M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.6335 | 5.4638 | 145.519 | 34.7793 | 7.1681 | Cell performance is degraded or low fill factor or hotspot formed over the cells or snail trails are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.2194 | 5.1019 | 123.5645 | 32.1523 | 6.7511
Difference | 2.3665 | 1.9562 | 69.481 | 1.2207 | 1.1319
Percentage Degradation | 8.1605 | 26.3643 | 32.3167 | 3.3908 | 13.6377

## Table 37
Module Number: AR19S7L4L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.4313 | 6.3103 | 173.1002 | 34.743 | 7.0947 | Cell performance is degraded or hotspot formed over the cells or snail trails are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.0057 | 5.8693 | 146.7653 | 32.1829 | 6.6544
Difference | 1.5687 | 1.1097 | 41.8998 | 1.257 | 1.2053
Percentage Degradation | 5.4093 | 14.9553 | 19.4883 | 3.4916 | 14.5222
Module Number: AR19S8L4U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 17.7592 | 6.3809 | 113.32 | 23.4769 | 7.3797 | Cell performance is degraded or one of the sub-string is open circuited or cells in sub- string burned or faulty bypass diode or snail trails are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 16.1001 | 5.9707 | 96.1291 | 21.6492 | 6.9667
Difference | 11.2408 | 1.0391 | 101.68 | 12.5231 | 0.9203
Percentage Degradation | 38.7613 | 14.0038 | 47.293 | 34.7864 | 11.0878

## Table 38
Module Number: AR19S9L1U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 18.224 | 5.5672 | 101.4573 | 24.0479 | 7.7767 | Cell performance is degraded or one of the sub-string is open circuited or cells in sub- string burned or faulty bypass diode or snail trails are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 16.4603 | 5.2063 | 85.6977 | 22.1085 | 7.3395
Difference | 10.776 | 1.8528 | 113.5427 | 11.9521 | 0.5233
Percentage Degradation | 37.1588 | 24.9697 | 52.8106 | 33.2003 | 6.305
Module Number: AR19S9L3U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.2992 | 6.4188 | 181.6483 | 35.8501 | 7.9431 | Burned cells or low fill factor or hotspot formed over the cells or snail trails are formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.1156 | 5.9649 | 149.8125 | 32.4891 | 7.4605
Difference | 0.7008 | 1.0012 | 33.3517 | 0.1499 | 0.3569
Percentage Degradation | 2.4166 | 13.4926 | 15.5124 | 0.4165 | 4.3002

## Table 39
Module Number: AR19S10L2L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.2138 | 6.3516 | 179.2027 | 35.8429 | 7.6595 | Cell performance is degraded or low fill factor or hotspot formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.8723 | 5.8862 | 146.4032 | 32.3054 | 7.1783
Difference | 0.7862 | 1.0684 | 35.7973 | 0.1571 | 0.6405
Percentage Degradation | 2.7111 | 14.3989 | 16.6499 | 0.4365 | 7.7167
Module Number: AR19S11L1U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 29.1304 | 6.275 | 182.7944 | 35.8471 | 7.5649 | Cell performance is degraded or low fill factor or hotspot formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 26.065 | 5.8175 | 151.6325 | 32.7035 | 7.0836
Difference | -0.1304 | 1.145 | 32.2056 | 0.1529 | 0.7351
Percentage Degradation | -0.4498 | 15.4309 | 14.9793 | 0.4248 | 8.8564

## Table 40
Module Number: AR19S11L2M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.7177 | 6.1177 | 175.686 | 35.5514 | 7.4779 | Cell performance is degraded or burned cells or hotspot formed over the cells or snail trails are formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.4822 | 5.7075 | 145.4389 | 32.2135 | 7.0514
Difference | 0.2823 | 1.3023 | 39.314 | 0.4486 | 0.8221
Percentage Degradation | 0.9735 | 17.5513 | 18.2856 | 1.2462 | 9.9043
Module Number: AR19S11L3L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 29.1903 | 6.079 | 177.4479 | 35.8268 | 7.2687 | Cell performance is degraded or burned cells or hotspot formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.7175 | 5.6512 | 145.334 | 32.2748 | 6.8337
Difference | -0.1903 | 1.341 | 37.5521 | 0.1732 | 1.0313
Percentage Degradation | -0.6563 | 18.0728 | 17.4661 | 0.481 | 12.4254

## Table 41
Module Number: AR19S11L4M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.2585 | 6.1781 | 168.4069 | 35.0058 | 7.3225 | Cell performance is degraded or snail trails are formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.5063 | 5.7294 | 140.4053 | 32.0604 | 6.8559
Difference | 1.7415 | 1.2419 | 46.5931 | 0.9942 | 0.9775
Percentage Degradation | 6.0052 | 16.7366 | 21.6712 | 2.7616 | 11.7772
Module Number: AR19S7L1U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.6124 | 6.3684 | 175.8483 | 35.3571 | 7.1195 | Cell performance is degraded or snail trails are formed over the cells or hotspots formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.8673 | 5.9198 | 147.2085 | 32.4279 | 6.6806
Difference | 1.3876 | 1.0516 | 39.1517 | 0.6429 | 1.1805
Percentage Degradation | 4.7847 | 14.1719 | 18.2101 | 1.7858 | 14.2229

## Table 42
Module Number: AR20S12L3L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.759 | 5.635 | 150.7872 | 35.5603 | 7.0408 | Cell performance is degraded or snail trails are formed over the cells or hotspots formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 23.6539 | 5.1256 | 121.2396 | 32.1217 | 6.475
Difference | 2.241 | 1.785 | 64.2128 | 0.4397 | 1.2592
Percentage Degradation | 7.7276 | 24.0565 | 29.8664 | 1.2214 | 15.1715
Module Number: AR20S10L1L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.2513 | 5.7486 | 162.406 | 35.4564 | 7.1347 | Cell performance is degraded or snail trails are formed over the cells or hotspots formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.2385 | 5.1051 | 128.846 | 32.3054 | 6.4004
Difference | 0.7487 | 1.6714 | 52.594 | 0.5436 | 1.1653
Percentage Degradation | 2.5818 | 22.5253 | 24.4623 | 1.51 | 14.0395

## Table 43
Module Number: AR20S9L2L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.4708 | 5.3945 | 153.5865 | 35.0517 | 6.3921 | Cell performance is degraded or snail trails are formed over the cells or hotspots formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.4656 | 4.8241 | 122.8497 | 31.9686 | 5.7737
Difference | 0.5292 | 2.0255 | 61.4135 | 0.9483 | 1.9079
Percentage Degradation | 1.8249 | 27.2974 | 28.5644 | 2.6341 | 22.9867
Module Number: AR20S9L1M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.5768 | 5.4183 | 149.4194 | 34.6097 | 7.2872 | Cell performance is degraded or hotspots formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.0222 | 4.9209 | 123.1307 | 31.9379 | 6.6765
Difference | 1.4232 | 2.0017 | 65.5806 | 1.3903 | 1.0128
Percentage Degradation | 4.9076 | 26.977 | 30.5026 | 3.862 | 12.2029

## Table 44
Module Number: AR20S8L4M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.6367 | 5.4651 | 156.5024 | 34.6998 | 7.1225 | Cell performance is degraded or burned cells or hotspots formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.9319 | 4.9209 | 127.6081 | 31.9686 | 6.471
Difference | 0.3633 | 1.9549 | 58.4976 | 1.3002 | 1.1775
Percentage Degradation | 1.2528 | 26.3463 | 27.2082 | 3.6118 | 14.1862
Module Number: AR20S8L2M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.89 | 5.5295 | 159.7473 | 34.8736 | 7.2471 | Cell performance is degraded or burned cells or hotspots formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 26.1543 | 4.9359 | 129.0943 | 32.1217 | 6.5274
Difference | 0.11 | 1.8905 | 55.2527 | 1.1264 | 1.0529
Percentage Degradation | 0.3794 | 25.4784 | 25.6989 | 3.1288 | 12.6859

## Table 45
Module Number: AR20S7L4L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.7053 | 5.6092 | 155.4053 | 34.7905 | 6.8264 | Cell performance is degraded or snail trails are formed over the cells or hotspots formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.1256 | 4.9668 | 124.7938 | 32.0911 | 6.0982
Difference | 1.2947 | 1.8108 | 59.5947 | 1.2095 | 1.4736
Percentage Degradation | 4.4646 | 24.4038 | 27.7184 | 3.3597 | 17.7543
Module Number: AR20S5L2M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.3496 | 6.0781 | 166.2329 | 34.754 | 7.3441 | Cell performance is degraded or burned cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.9505 | 5.503 | 137.3016 | 32.2135 | 6.7047
Difference | 1.6504 | 1.3419 | 48.7671 | 1.246 | 0.9559
Percentage Degradation | 5.6911 | 18.0852 | 22.6824 | 3.4611 | 11.5167

## Table 46
Module Number: AR20S5L2L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.6842 | 6.211 | 165.7353 | 34.3981 | 6.6231 | Cell performance is degraded or snail trails are formed over the cells or hotspots formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.5651 | 5.6139 | 137.9058 | 32.1217 | 6.0316
Difference | 2.3158 | 1.209 | 49.2647 | 1.6019 | 1.6769
Percentage Degradation | 7.9856 | 16.2939 | 22.9138 | 4.4498 | 20.2037
Module Number: AR20S3L1M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.3987 | 5.8047 | 164.8462 | 34.6805 | 7.1451 | Cell performance is degraded or snail trails are formed over the cells or hotspots formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 26.0648 | 5.2228 | 136.1305 | 32.3054 | 6.479
Difference | 0.6013 | 1.6153 | 50.1538 | 1.3195 | 1.1549
Percentage Degradation | 2.0736 | 21.7693 | 23.3273 | 3.6654 | 13.915

## Table 47
Module Number: AR20S3L2M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 25.7772 | 5.077 | 130.8707 | 34.1877 | 6.3996 | Cell performance is degraded or snail trails are formed over the cells or hotspots formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 23.6585 | 4.5322 | 107.225 | 31.8461 | 5.7576
Difference | 3.2228 | 2.343 | 84.1293 | 1.8123 | 1.9004
Percentage Degradation | 11.1132 | 31.5768 | 39.1299 | 5.0341 | 22.8967
Module Number: AR20S3L2L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.6286 | 5.3072 | 141.3239 | 34.6198 | 6.9995 | Cell performance is degraded or snail trails are formed over the cells or hotspots formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.4076 | 4.7284 | 115.4081 | 32.2135 | 6.2856
Difference | 2.3714 | 2.1128 | 73.6761 | 1.3802 | 1.3005
Percentage Degradation | 8.1772 | 28.4741 | 34.2679 | 3.8338 | 15.6692

## Table 48
Module Number: AR20S2L4L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.8609 | 5.5427 | 159.9668 | 34.9924 | 7.0191 | Cell performance is degraded or snail trails are formed over the cells or hotspots formed over the cells or low fill factor or burned cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 26.1712 | 4.9498 | 129.5415 | 32.2748 | 6.3239
Difference | 0.1391 | 1.8773 | 55.0332 | 1.0076 | 1.2809
Percentage Degradation | 0.4797 | 25.3007 | 25.5968 | 2.7989 | 15.433
Module Number: AR20S2L3U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.0197 | 6.4007 | 172.9458 | 34.6339 | 7.1699 | Cell performance is degraded or snail trails are formed over the cells or hotspots formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.9258 | 5.713 | 142.402 | 32.3973 | 6.4468
Difference | 1.9803 | 1.0193 | 42.0542 | 1.3661 | 1.1301
Percentage Degradation | 6.8285 | 13.7369 | 19.5601 | 3.7947 | 13.6158

## Table 49
Module Number: AR21S3L1L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.6842 | 5.9273 | 164.0926 | 34.8969 | 6.4513 | Cell performance degraded or snail trails are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.3629 | 5.3307 | 135.2016 | 32.4585 | 5.8483
Difference | 1.3158 | 1.4927 | 50.9074 | 1.1031 | 1.8487
Percentage Degradation | 4.5372 | 20.1172 | 23.6778 | 3.0643 | 22.2735
Module Number: AR21S6L1L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.2613 | 5.0669 | 138.1306 | 35.3638 | 6.843 | Cell performance is degraded or snail trails are formed over the cells or hotspots formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.6588 | 4.5486 | 112.1634 | 32.5504 | 6.1989
Difference | 1.7387 | 2.3531 | 76.8694 | 0.6362 | 1.457
Percentage Degradation | 5.9955 | 31.7128 | 35.7532 | 1.7674 | 17.5539

## Table 50
Module Number: AR21S9L2M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 29.4635 | 5.0734 | 149.4806 | 35.8347 | 6.8861 | Cell performance is degraded or snail trails are formed over the cells or burned cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 26.1626 | 4.679 | 122.4157 | 32.4891 | 6.4186
Difference | -0.4635 | 2.3466 | 65.5194 | 0.1653 | 1.4139
Percentage Degradation | -1.5983 | 31.6252 | 30.4741 | 0.4592 | 17.0348
Module Number: AR21S11L1M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.7 | 6.2254 | 172.4429 | 35.8412 | 7.1625 | Cell performance is degraded or snail trails are formed over the cells or hotspots formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.648 | 5.7583 | 141.9317 | 32.5504 | 6.6947
Difference | 1.3 | 1.1946 | 42.5571 | 0.1588 | 1.1375
Percentage Degradation | 4.4827 | 16.1001 | 19.794 | 0.4412 | 13.705

## Table 51
Module Number: AR21S11L3M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 29.8617 | 5.552 | 165.791 | 35.8409 | 7.1412 | Cell performance is degraded or hotspot formed over the cells or low fill factor or burned cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 26.4799 | 5.1368 | 136.0234 | 32.4585 | 6.6785
Difference | -0.8617 | 1.868 | 49.209 | 0.1591 | 1.1588
Percentage Degradation | -2.9714 | 25.1757 | 22.8879 | 0.4419 | 13.9612
Module Number: AR21S12L3U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.0549 | 6.5849 | 184.7397 | 35.8383 | 7.5608 | Cell performance is degraded or snail trails formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.1677 | 6.0765 | 152.9302 | 32.7647 | 7.0453
Difference | 0.9451 | 0.8351 | 30.2603 | 0.1617 | 0.7392
Percentage Degradation | 3.2589 | 11.2543 | 14.0746 | 0.4492 | 8.9064

## Table 52
Module Number: AR20S2L4L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.6923 | 5.4297 | 155.7919 | 35.8351 | 7.2222 | Cell performance is degraded or hotspot formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.3304 | 5.012 | 126.9572 | 32.336 | 6.741
Difference | 0.3077 | 1.9903 | 59.2081 | 0.1649 | 1.0778
Percentage Degradation | 1.0609 | 26.8229 | 27.5387 | 0.4581 | 12.9856
Module Number: AR22S9L2U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.1465 | 6.7903 | 184.3328 | 35.4986 | 7.3703 | Cell performance is degraded or snail trails formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.2162 | 6.0499 | 146.5059 | 32.3054 | 6.6342
Difference | 1.8535 | 0.6297 | 30.6672 | 0.5014 | 0.9297
Percentage Degradation | 6.3914 | 8.4866 | 14.2638 | 1.3929 | 11.2007

## Table 53
Module Number: AR22S8L1U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 29.0646 | 5.9589 | 173.1942 | 35.756 | 7.3035 | Cell performance is degraded or snail trails formed over the cells or low fill factor or burned cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.7286 | 5.2909 | 136.1286 | 32.336 | 6.5556
Difference | -0.0646 | 1.4611 | 41.8058 | 0.244 | 0.9965
Percentage Degradation | -0.2227 | 19.6908 | 19.4446 | 0.6778 | 12.0065
Module Number: AR22S7L4L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.9662 | 6.0555 | 169.3485 | 35.1142 | 6.7965 | Cell performance is degraded or snail trails are formed over the cells or hotspots formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.1062 | 5.3595 | 134.5576 | 32.1217 | 6.074
Difference | 1.0338 | 1.3645 | 45.6515 | 0.8858 | 1.5035
Percentage Degradation | 3.5648 | 18.3899 | 21.2333 | 2.4607 | 18.1147

## Table 54
Module Number: AR22S7L2U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.9705 | 6.0982 | 170.5692 | 35.2293 | 6.8643 | Cell performance is degraded or snail trails are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.0681 | 5.3894 | 135.1011 | 32.1829 | 6.1264
Difference | 1.0295 | 1.3218 | 44.4308 | 0.7707 | 1.4357
Percentage Degradation | 3.5499 | 17.8144 | 20.6655 | 2.1408 | 17.298
Module Number: AR22S6L1L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.3604 | 5.0958 | 139.4241 | 35.7652 | 7.8228 | Cell performance is degraded or snail trails are formed over the cells or hotspots formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.6059 | 4.5328 | 111.5336 | 32.7647 | 7.0252
Difference | 1.6396 | 2.3242 | 75.5759 | 0.2348 | 0.4772
Percentage Degradation | 5.6539 | 31.3229 | 35.1516 | 0.6521 | 5.7495

## Table 55
Module Number: AR22S4L2M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 29.8802 | 5.4541 | 162.9693 | 35.6884 | 6.7848 | Cell performance is degraded or snail trails are formed over the cells or hotspots formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 26.6351 | 4.8936 | 130.3428 | 32.4585 | 6.1505
Difference | -0.8802 | 1.9659 | 52.0307 | 0.3116 | 1.5152
Percentage Degradation | -3.0353 | 26.4948 | 24.2003 | 0.8655 | 18.2559
Module Number: AR22S3L1L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.1144 | 6.0149 | 169.1054 | 35.3406 | 6.8071 | Cell performance is degraded or snail trails are formed over the cells or hotspot formed on the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.1877 | 5.2474 | 132.1694 | 32.2748 | 5.9974
Difference | 0.8856 | 1.4051 | 45.8946 | 0.6594 | 1.4929
Percentage Degradation | 3.0536 | 18.9367 | 21.3463 | 1.8316 | 17.9866

## Table 56
Module Number: AR22S2L3L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.8535 | 6.1927 | 178.6816 | 35.7392 | 7.4799 | Cell performance is degraded or snail trails are formed over the cells or hotspot formed on the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.4972 | 5.4555 | 139.0989 | 32.2748 | 6.6624
Difference | 0.1465 | 1.2273 | 36.3184 | 0.2608 | 0.8201
Percentage Degradation | 0.5052 | 16.5402 | 16.8923 | 0.7245 | 9.8804
Module Number: AR22S1L4L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.2465 | 5.7669 | 157.127 | 34.7207 | 7.5053 | Cell performance is degraded or hotspot formed on the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.8567 | 4.9585 | 123.2531 | 32.1829 | 6.5072
Difference | 1.7535 | 1.6531 | 57.873 | 1.2793 | 0.7947
Percentage Degradation | 6.0465 | 22.2795 | 26.9177 | 3.5536 | 9.5742

## Table 57
Module Number: AR23S1L2L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.2133 | 6.1266 | 172.8509 | 35.1465 | 7.1859 | Cell performance is degraded or snail trails are formed over the cells or hotspot formed on the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.6535 | 5.2603 | 134.9445 | 32.4891 | 6.2231
Difference | 0.7867 | 1.2934 | 42.1491 | 0.8535 | 1.1141
Percentage Degradation | 2.7127 | 17.4316 | 19.6042 | 2.3707 | 13.4234
Module Number: AR23S1L3L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.8389 | 5.4387 | 151.4076 | 34.7266 | 7.2786 | Cell performance is degraded or snail trails are formed over the cells or hotspot formed on the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.4803 | 4.6158 | 117.6109 | 32.2748 | 6.2271
Difference | 1.1611 | 1.9813 | 63.5924 | 1.2734 | 1.0214
Percentage Degradation | 4.0037 | 26.7021 | 29.5779 | 3.5371 | 12.3057

## Table 58
Module Number: AR23S1L4U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.5421 | 5.8252 | 166.2643 | 34.7225 | 7.4187 | Cell performance is degraded or hotspot formed on the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 26.2183 | 4.9258 | 129.1451 | 32.3666 | 6.3218
Difference | 0.4579 | 1.5948 | 48.7357 | 1.2775 | 0.8813
Percentage Degradation | 1.5788 | 21.493 | 22.6678 | 3.5487 | 10.6179
Module Number: AR23S6L3M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.4354 | 6.1626 | 169.0738 | 35.1321 | 6.7607 | Cell performance is degraded or hotspot formed on the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.93 | 5.4033 | 134.7039 | 32.4585 | 5.9793
Difference | 1.5646 | 1.2574 | 45.9262 | 0.8679 | 1.5393
Percentage Degradation | 5.3951 | 16.946 | 21.361 | 2.4109 | 18.5456

## Table 59
Module Number: AR23S6L3U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.1987 | 6.1242 | 172.693 | 34.9423 | 7.3696 | Cell performance is degraded or snail trails are formed over the cells or hotspot formed on the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.8823 | 5.3356 | 138.0985 | 32.5504 | 6.471
Difference | 0.8013 | 1.2958 | 42.307 | 1.0577 | 0.9304
Percentage Degradation | 2.7632 | 17.4642 | 19.6777 | 2.9379 | 11.2095
Module Number: AR23S8L3M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.7031 | 5.3363 | 153.1677 | 34.7014 | 6.6289 | Cell performance is degraded or burned cells or hotspot formed on the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 26.3857 | 4.5721 | 120.639 | 32.3666 | 5.7233
Difference | 0.2969 | 2.0837 | 61.8323 | 1.2986 | 1.6711
Percentage Degradation | 1.0237 | 28.0826 | 28.7592 | 3.6073 | 20.1339

## Table 60
Module Number: AR23S7L4L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 8.245 | 5.4182 | 44.6729 | 19.5633 | 5.6775 | Cell performance is degraded or one of the end of sub-string is open circuited or cells in sub-string burned or faulty bypass diode.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 7.55 | 4.5751 | 34.542 | 18.189 | 4.8326
Difference | 20.755 | 2.0018 | 170.3271 | 16.4367 | 2.6225
Percentage Degradation | 71.5689 | 26.9787 | 79.2219 | 45.6574 | 31.5966
Module Number: AR23S9L1U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 29.4451 | 5.2951 | 155.9143 | 35.3547 | 6.5302 | Cell performance is degraded or snail trails are formed over the cells or hotspot formed on the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 26.6118 | 4.4302 | 117.897 | 32.5198 | 5.5137
Difference | -0.4451 | 2.1249 | 59.0857 | 0.6453 | 1.7698
Percentage Degradation | -1.5348 | 28.6377 | 27.4817 | 1.7926 | 21.3226

## Table 61
Module Number: AR23S9L2L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 29.1916 | 5.7369 | 167.4699 | 35.6331 | 6.8474 | Cell performance is degraded or hotspot formed on the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 26.2212 | 4.7792 | 125.3171 | 32.6116 | 5.7596
Difference | -0.1916 | 1.6831 | 47.5301 | 0.3669 | 1.4526
Percentage Degradation | -0.6607 | 22.683 | 22.107 | 1.0191 | 17.5014
Module Number: AR23S9L4M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 29.3347 | 5.9027 | 173.1541 | 35.4014 | 7.3081 | Cell performance is degraded or hotspot formed on the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 26.4084 | 4.5147 | 119.2255 | 32.4585 | 5.6427
Difference | -0.3347 | 1.5173 | 41.8459 | 0.5986 | 0.9919
Percentage Degradation | -1.1541 | 20.4487 | 19.4632 | 1.6627 | 11.9506

## Table 62
Module Number: AR23S10L3U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 21.2485 | 5.9611 | 126.6633 | 33.1697 | 7.5316 | Increased series resistance or hotspot and snail tarils formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 19.4777 | 4.5512 | 88.6462 | 30.8662 | 5.7959
Difference | 7.7515 | 1.4589 | 88.3367 | 2.8303 | 0.7684
Percentage Degradation | 26.7294 | 19.6623 | 41.0868 | 7.862 | 9.2579
Module Number: AR23S11L3U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.6396 | 6.3494 | 181.8444 | 35.4532 | 7.4483 | Cell performance is degraded or snail trails are formed over the cells or hotspot formed on the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.9444 | 4.8305 | 125.3242 | 32.6729 | 5.7173
Difference | 0.3604 | 1.0706 | 33.1556 | 0.5468 | 0.8517
Percentage Degradation | 1.2429 | 14.4284 | 15.4212 | 1.519 | 10.2618

## Table 63
Module Number: AR23S12L1L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.2046 | 4.988 | 140.6836 | 35.4486 | 7.6955 | Cell performance is degraded or snail trails are formed over the cells or hotspot formed on the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.4667 | 3.7961 | 96.6732 | 32.581 | 5.9107
Difference | 0.7954 | 2.432 | 74.3164 | 0.5514 | 0.6045
Percentage Degradation | 2.7428 | 32.7767 | 34.5657 | 1.5317 | 7.2836
Module Number: AR27S4L2U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.9519 | 5.5047 | 159.3705 | 35.0111 | 6.8733 | Cell performance is degraded or hotspot formed on the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 26.6315 | 4.6275 | 123.2366 | 32.6729 | 5.8221
Difference | 0.0481 | 1.9153 | 55.6295 | 0.9889 | 1.4267
Percentage Degradation | 0.1659 | 25.8131 | 25.8742 | 2.7468 | 17.1897

## Table 64
Module Number: AR28S2L1L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.4539 | 4.5145 | 128.4557 | 34.4803 | 7.4245 | Cell performance is degraded or hotspot formed on the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 26.3304 | 3.767 | 99.188 | 32.336 | 6.2392
Difference | 0.5461 | 2.9055 | 86.5443 | 1.5197 | 0.8755
Percentage Degradation | 1.8832 | 39.1574 | 40.2532 | 4.2213 | 10.5486
Module Number: AR28S6L4U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 21.8026 | 5.8732 | 128.0517 | 33.3975 | 7.0364 | Cell performance is degraded or snail trails are formed on the cells or low fill factor or increased cell resistance of module.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 20.0595 | 4.5475 | 91.2201 | 31.1724 | 5.4895
Difference | 7.1974 | 1.5468 | 86.9483 | 2.6025 | 1.2636
Percentage Degradation | 24.8186 | 20.846 | 40.4411 | 7.2292 | 15.2243

## Table 65
Module Number: AR28S7L4U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.5219 | 5.0195 | 143.1655 | 34.4203 | 8.3577 | Burned cells or low fill factor or hotspot formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 26.1449 | 3.8846 | 101.5613 | 32.0298 | 6.5193
Difference | 0.4781 | 2.4005 | 71.8345 | 1.5797 | -0.0577
Percentage Degradation | 1.6485 | 32.3519 | 33.4114 | 4.388 | -0.6955
Module Number: AR28S12L1M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.6944 | 5.7191 | 158.3882 | 34.5333 | 7.7657 | Cell performance is degraded or hotspot formed on the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.2262 | 4.3929 | 110.8169 | 31.9686 | 6.0155
Difference | 1.3056 | 1.7009 | 56.6118 | 1.4667 | 0.5343
Percentage Degradation | 4.5019 | 22.9227 | 26.3311 | 4.0741 | 6.4375

## Table 66
Module Number: AR29S10L2L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 25.3979 | 6.8093 | 172.9413 | 35.4582 | 8.1759 | Hotspot formed on the cells or low fill factor or increased series resistance of module.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 22.9775 | 5.1978 | 119.4329 | 32.6422 | 6.2977
Difference | 3.6021 | 0.6107 | 42.0587 | 0.5418 | 0.1241
Percentage Degradation | 12.4209 | 8.2309 | 19.5622 | 1.505 | 1.4953
Module Number: AR29S7L4M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.1299 | 5.0193 | 141.1923 | 33.9246 | 7.6301 | Cell performance is degraded or hotspot formed on the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 26.0922 | 3.8195 | 99.6583 | 31.8767 | 5.8462
Difference | 0.8701 | 2.4007 | 73.8077 | 2.0754 | 0.6699
Percentage Degradation | 3.0003 | 32.3545 | 34.3292 | 5.765 | 8.0709

## Table 67
Module Number: AR30S8L3M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.3493 | 5.2763 | 149.5781 | 35.4261 | 6.924 | Cell performance is degraded or snail trails are formed on the cells or low fill factor or increased cell resistance of module or burned cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.6172 | 3.9732 | 101.7809 | 32.581 | 5.2618
Difference | 0.6507 | 2.1437 | 65.4219 | 0.5739 | 1.376
Percentage Degradation | 2.2439 | 28.8914 | 30.4288 | 1.5942 | 16.5779
Module Number: AR30S8L1M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.7613 | 5.7948 | 166.6661 | 35.2487 | 6.3421 | Cell performance is degraded or snail trails are formed on the cells or hotspot formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.8494 | 4.3205 | 111.6825 | 32.2748 | 4.7741
Difference | 0.2387 | 1.6252 | 48.3339 | 0.7513 | 1.9579
Percentage Degradation | 0.8232 | 21.9028 | 22.4809 | 2.0869 | 23.5895

## Table 68
Module Number: AR30S6L1L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.6224 | 4.9928 | 132.9195 | 34.4942 | 5.8652 | Cell performance is degraded or snail trails are formed on the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.7087 | 3.7501 | 92.6603 | 32.4279 | 4.4356
Difference | 2.3776 | 2.4272 | 82.0805 | 1.5058 | 2.4348
Percentage Degradation | 8.1985 | 32.7121 | 38.177 | 4.1829 | 29.3347
Module Number: AR30S5L4U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.7348 | 5.0345 | 139.6312 | 35.2711 | 6.444 | Cell performance is degraded or snail trails are formed on the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.2542 | 3.7842 | 95.5682 | 32.6422 | 4.885
Difference | 1.2652 | 2.3855 | 75.3688 | 0.7289 | 1.856
Percentage Degradation | 4.3627 | 32.1495 | 35.0553 | 2.0247 | 22.3614

## Table 69
Module Number: AR30S3L1M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 24.992 | 6.9569 | 173.8665 | 35.4326 | 7.7845 | Cell performance is degraded or Increased series resistance of the module.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 23.4078 | 5.1558 | 120.6853 | 33.5609 | 5.8039
Difference | 4.008 | 0.4631 | 41.1335 | 0.5674 | 0.5155
Percentage Degradation | 13.8207 | 6.2414 | 19.1319 | 1.5761 | 6.2114
Module Number: AR31S1L3U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.3871 | 5.5316 | 156.8096 | 35.3967 | 7.1716 | Cell performance is degraded or snail trails are formed on the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 26.3745 | 3.8859 | 102.4881 | 32.581 | 5.7092
Difference | 0.6129 | 1.8884 | 58.1904 | 0.6033 | 1.1284
Percentage Degradation | 2.1135 | 25.4499 | 27.0653 | 1.6757 | 13.5949

## Table 70
Module Number: AR33S2L1L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.3415 | 6.4777 | 183.5877 | 35.126 | 8.3295 | Hotspot Formed over the cells or low fill factor of module.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 26.2628 | 4.2909 | 112.6899 | 32.9791 | 5.556
Difference | 0.6585 | 0.9423 | 31.4123 | 0.874 | -0.0295
Percentage Degradation | 2.2708 | 12.6994 | 14.6104 | 2.4278 | -0.3556
Module Number: AR33S3L4L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.3825 | 6.1052 | 173.2808 | 35.1357 | 7.4174 | Cell performance is degraded or hotspot formed over the cells or low fill factor of module.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 26.1138 | 4.0925 | 106.8703 | 32.7953 | 5.0099
Difference | 0.6175 | 1.3148 | 41.7192 | 0.8643 | 0.8826
Percentage Degradation | 2.1293 | 17.7197 | 19.4043 | 2.4007 | 10.634

## Table 71
Module Number: AR33S4L1U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 29.9137 | 6.2078 | 185.6994 | 35.2152 | 8.2705 | Cell performance is degraded or hotspot formed over the cells or low fill factor of module or burned cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 27.7279 | 4.1671 | 115.545 | 33.0709 | 5.5903
Difference | -0.9137 | 1.2122 | 29.3006 | 0.7848 | 0.0295
Percentage Degradation | -3.1507 | 16.3364 | 13.6282 | 2.18 | 0.3556
Module Number: AR33S4L3U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 25.5054 | 5.9075 | 150.6725 | 35.1557 | 7.9874 | Increased series resistance of the module or low fill factor or hotspot formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 23.3971 | 3.9899 | 93.3528 | 32.7341 | 5.4371
Difference | 3.4946 | 1.5125 | 64.3275 | 0.8443 | 0.3126
Percentage Degradation | 12.0505 | 20.3843 | 29.9198 | 2.3452 | 3.7668

## Table 72
Module Number: AR34S1L2U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.0762 | 6.9321 | 194.6284 | 35.5985 | 8.5734 | Increased series resistance of the module or low fill factor or hotspot formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.3942 | 5.6646 | 143.849 | 32.7647 | 7.0695
Difference | 0.9238 | 0.4879 | 20.3716 | 0.4015 | -0.2734
Percentage Degradation | 3.1855 | 6.5749 | 9.4752 | 1.1152 | -3.2935
Module Number: AR34S1L2M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.2643 | 7.0762 | 185.8507 | 35.6171 | 8.0988 | Increased series resistance of the module or low fill factor or hotspot formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 23.8486 | 5.83 | 139.0369 | 32.8872 | 6.7309
Difference | 2.7357 | 0.3438 | 29.1493 | 0.3829 | 0.2012
Percentage Degradation | 9.4336 | 4.6337 | 13.5578 | 1.0636 | 2.4242

## Table 73
Module Number: AR34S3L2L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.1179 | 5.7553 | 161.8257 | 35.0992 | 6.9955 | Cell performance is degraded or hotspot formed over the cells or low fill factor of module or snail trails formed on the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.7853 | 4.7178 | 121.6488 | 32.6729 | 5.7797
Difference | 0.8821 | 1.6647 | 53.1743 | 0.9008 | 1.3045
Percentage Degradation | 3.0418 | 22.4358 | 24.7322 | 2.5021 | 15.7165
Module Number: AR34S3L3L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.8426 | 5.4081 | 155.9839 | 34.9228 | 6.5562 | Cell performance is degraded or hotspot formed over the cells or low fill factor of module or burned cells or snail tarils formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 26.4914 | 4.4455 | 117.7672 | 32.5504 | 5.4311
Difference | 0.1574 | 2.0119 | 59.0161 | 1.0772 | 1.7438
Percentage Degradation | 0.5426 | 27.1145 | 27.4493 | 2.9923 | 21.0091

## Table 74
Module Number: AR34S4L1U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.4896 | 6.7136 | 177.8405 | 35.612 | 7.8524 | Light cell performance is degraded or hotspot formed over the cells or low fill factor of module or burned cells or snail tarils formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.1121 | 5.513 | 132.929 | 32.9484 | 6.5032
Difference | 2.5104 | 0.7064 | 37.1595 | 0.388 | 0.4476
Percentage Degradation | 8.6567 | 9.5201 | 17.2835 | 1.0779 | 5.3926
Module Number: AR34S4L4L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 29.1016 | 5.7432 | 167.136 | 35.5637 | 7.8323 | Cell performance is degraded or hotspot formed over the cells or low fill factor of module or burned cells or snail tarils formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 26.1727 | 4.6546 | 121.8223 | 32.581 | 6.4085
Difference | -0.1016 | 1.6768 | 47.864 | 0.4363 | 0.4677
Percentage Degradation | -0.3503 | 22.5985 | 22.2623 | 1.2121 | 5.6349

## Table 75
Module Number: AR34S7L2U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.2452 | 6.4183 | 181.2855 | 35.3251 | 7.9278 | Hotspot formed over the cells or low fill factor or bubbles are formed at backsheet of module.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.7592 | 5.5141 | 142.0377 | 32.7341 | 6.868
Difference | 0.7548 | 1.0017 | 33.7145 | 0.6749 | 0.3722
Percentage Degradation | 2.6028 | 13.5003 | 15.6812 | 1.8748 | 4.4849
Module Number: AR33S7L4M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.3635 | 5.9191 | 161.9674 | 34.5285 | 7.9564 | Hotspot formed on the cells or bubbles are formed at backsheet of module or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.3076 | 5.1133 | 129.4054 | 32.3666 | 6.9224
Difference | 1.6365 | 1.5009 | 53.0326 | 1.4715 | 0.3436
Percentage Degradation | 5.6432 | 20.2277 | 24.6663 | 4.0876 | 4.1403

## Table 76
Module Number: BR36S1L3L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.2748 | 4.108 | 112.0443 | 34.6053 | 6.6085 | Cell performance is degraded or burned cells or snail trails are formed on the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.4471 | 3.4928 | 88.8828 | 32.6729 | 5.6548
Difference | 1.7252 | 3.312 | 102.9557 | 1.3947 | 1.6915
Percentage Degradation | 5.9489 | 44.6364 | 47.8864 | 3.8742 | 20.3795
Module Number: BR36S2L1M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 17.7581 | 6.4832 | 115.1295 | 24.8155 | 6.9833 | Cell performance is degraded or one of the sub-string is open circuited or cells in sub- string burned or faulty bypass diode or snail trails formed on the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 16.4591 | 5.6037 | 92.2321 | 23.3028 | 6.078
Difference | 11.2419 | 0.9368 | 99.8705 | 11.1845 | 1.3167
Percentage Degradation | 38.7653 | 12.6251 | 46.4514 | 31.0682 | 15.864

## Table 77
Module Number: BR36S2L4L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.3025 | 5.0833 | 138.7861 | 34.4095 | 6.4982 | Cell performance is degraded or hotspots formed on the cells or snail trails are formed on the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.2991 | 4.4101 | 111.5704 | 32.3054 | 5.677
Difference | 1.6975 | 2.3367 | 76.2139 | 1.5905 | 1.8018
Percentage Degradation | 5.8534 | 31.4923 | 35.4483 | 4.4181 | 21.7088
Module Number: BR36S3L1U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 16.9657 | 6.0642 | 102.8839 | 23.3708 | 7.3283 | Cell performance is degraded or one of the sub-string is open circuited or cells in sub- string burned or faulty bypass diode or snail trails formed on the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 15.6794 | 5.2369 | 82.1112 | 21.8942 | 6.3742
Difference | 12.0343 | 1.3558 | 112.1161 | 12.6292 | 0.9717
Percentage Degradation | 41.4976 | 18.2719 | 52.147 | 35.081 | 11.7068

## Table 78
Module Number: BR36S6L1U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 29.2386 | 5.7563 | 168.3062 | 35.523 | 7.1305 | Cell performance is degraded or hotspots formed on the cells or snail trails are formed on the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 26.484 | 4.992 | 132.2086 | 32.7341 | 6.2392
Difference | -0.2386 | 1.6637 | 46.6938 | 0.477 | 1.1695
Percentage Degradation | -0.8228 | 22.4219 | 21.7181 | 1.3249 | 14.0908
Module Number: BR36S6L2L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.687 | 5.8191 | 161.114 | 35.0239 | 6.5173 | Cell performance is degraded or snail trails are formed on the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.3697 | 5.0823 | 128.9356 | 32.581 | 5.7374
Difference | 1.313 | 1.6009 | 53.886 | 0.9761 | 1.7827
Percentage Degradation | 4.5276 | 21.5752 | 25.0633 | 2.7115 | 21.4783

## Table 79
Module Number: BR36S6L3M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.7051 | 6.5337 | 181.0167 | 34.4575 | 7.9124 | Hotspot are formed over the cells or snail trails are formed on the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.8355 | 5.2085 | 134.5634 | 32.5198 | 6.348
Difference | 1.2949 | 0.8863 | 33.9833 | 1.5425 | 0.3876
Percentage Degradation | 4.4652 | 11.9448 | 15.8062 | 4.2847 | 4.6704
Module Number: BR36S6L3U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.8107 | 6.4106 | 178.283 | 34.339 | 7.446 | Hotspots are formed over the cells or cell performance degraded.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.8343 | 5.0857 | 131.3843 | 32.3054 | 5.947
Difference | 1.1893 | 1.0094 | 36.717 | 1.661 | 0.854
Percentage Degradation | 4.1012 | 13.6038 | 17.0777 | 4.6139 | 10.2896

## Table 80
Module Number: BR35S8L4U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.2576 | 6.3056 | 171.8766 | 34.9934 | 7.1259 | Cell performance is degraded or snail trails are formed on the cells or low fill factor or burned cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.0314 | 6.0853 | 152.3238 | 32.6116 | 6.9305
Difference | 1.7424 | 1.1144 | 43.1234 | 1.0066 | 1.1741
Percentage Degradation | 6.0082 | 15.0184 | 20.0574 | 2.7962 | 14.1454
Module Number: BR35S8L3U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 17.8258 | 8.0407 | 143.3319 | 23.8647 | 8.7839 | One of the sub-string is open circuited or cells in sub-string burned or faulty bypass diode or snail trails formed on the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 16.4163 | 6.3754 | 104.6599 | 22.2923 | 7.0171
Difference | 11.1742 | -0.6207 | 71.6681 | 12.1353 | -0.4839
Percentage Degradation | 38.5319 | -8.3654 | 33.334 | 33.709 | -5.8305

## Table 81
Module Number: BR35S8L2L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 25.714 | 5.9182 | 152.1807 | 33.8941 | 7.9204 | Increased shunt and series resistance or hotspot formed over the cells or snail trails formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 23.6822 | 4.7094 | 111.5295 | 31.6624 | 6.3501
Difference | 3.286 | 1.5018 | 62.8193 | 2.1059 | 0.3796
Percentage Degradation | 11.3311 | 20.2398 | 29.2183 | 5.8498 | 4.5739
Module Number: BR35S4L2M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.2405 | 4.7189 | 128.5447 | 34.5224 | 7.6773 | Cell performance is degraded or snail trails are formed on the cells or low fill factor or burned cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.2862 | 3.8298 | 96.8419 | 32.4585 | 6.2735
Difference | 1.7595 | 2.7011 | 86.4553 | 1.4776 | 0.6227
Percentage Degradation | 6.0673 | 36.4032 | 40.2118 | 4.1044 | 7.502

## Table 82
Module Number: BR35S2L2L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.5196 | 6.1826 | 163.9614 | 34.6376 | 6.7371 | Cell performance is degraded or hotspot formed on the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.2081 | 5.7226 | 138.5342 | 32.1217 | 6.2876
Difference | 2.4804 | 1.2374 | 51.0386 | 1.3624 | 1.5629
Percentage Degradation | 8.5531 | 16.6759 | 23.7389 | 3.7844 | 18.8305
Module Number: BR34S1L4U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 29.9911 | 5.0504 | 151.4683 | 35.8836 | 6.8082 | Cell performance is degraded or snail trails are formed on the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 26.8937 | 4.7668 | 128.1983 | 32.7953 | 6.4891
Difference | -0.9911 | 2.3696 | 63.5317 | 0.1164 | 1.4918
Percentage Degradation | -3.4176 | 31.9348 | 29.5496 | 0.3232 | 17.9735

## Table 83
Module Number: BR34S5L4M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 18.5145 | 5.5164 | 102.1337 | 35.4423 | 5.8858 | Cell performance is degraded or one of the end of sub-string is open circuited or cells in sub-string burned or faulty bypass diode or snail trails formed on the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 16.6249 | 5.1628 | 85.8311 | 32.4279 | 5.5621
Difference | 10.4855 | 1.9036 | 112.8663 | 0.5577 | 2.4142
Percentage Degradation | 36.1569 | 25.6548 | 52.496 | 1.5493 | 29.0862
Module Number: BR34S6L1U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.4809 | 5.3463 | 146.9216 | 35.8717 | 6.9733 | Cell performance is degraded or snail trails are formed on the cells or hotspot formed on the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.5402 | 5.0182 | 123.148 | 32.6729 | 6.612
Difference | 1.5191 | 2.0737 | 68.0784 | 0.1283 | 1.3267
Percentage Degradation | 5.2383 | 27.9472 | 31.6644 | 0.3564 | 15.9845

## Table 84
Module Number: BR33S1L1M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 29.1376 | 5.7396 | 167.2386 | 35.8986 | 6.7928 | Cell performance is degraded or snail trails are formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.9063 | 5.4611 | 141.4761 | 32.581 | 6.5314
Difference | -0.1376 | 1.6804 | 47.7614 | 0.1014 | 1.5072
Percentage Degradation | -0.4746 | 22.6468 | 22.2146 | 0.2818 | 18.1587
Module Number: BR33S1L2U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 29.0808 | 5.5497 | 161.3898 | 35.9095 | 6.7102 | Cell performance is degraded or hotspot are formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.8462 | 5.3089 | 137.2148 | 32.581 | 6.4871
Difference | -0.0808 | 1.8703 | 53.6102 | 0.0905 | 1.5898
Percentage Degradation | -0.2787 | 25.2062 | 24.935 | 0.2514 | 19.1536

## Table 85
Module Number: BR33S1L4U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.7612 | 5.6891 | 152.2472 | 35.9005 | 6.7242 | Cell performance is degraded or hotspot are formed over the cells or low fill factor or snail trails are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 23.7644 | 5.4187 | 128.7732 | 32.5504 | 6.473
Difference | 2.2388 | 1.7309 | 62.7528 | 0.0995 | 1.5758
Percentage Degradation | 7.7201 | 23.3274 | 29.1873 | 0.2763 | 18.985
Module Number: BR33S2L3L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.6126 | 5.5107 | 152.1658 | 34.8826 | 6.3555 | Cell performance is degraded or hotspot are formed over the cells or low fill factor or snail trails are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.0482 | 5.191 | 130.0243 | 32.1829 | 6.0397
Difference | 1.3874 | 1.9093 | 62.8342 | 1.1174 | 1.9445
Percentage Degradation | 4.7841 | 25.7313 | 29.2252 | 3.1039 | 23.4271

## Table 86
Module Number: BR33S3L1U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.5452 | 5.7024 | 162.7771 | 35.4768 | 7.1425 | Cell performance is degraded or hotspot are formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.5422 | 5.2696 | 134.5965 | 32.3666 | 6.6665
Difference | 0.4548 | 1.7176 | 52.2229 | 0.5232 | 1.1575
Percentage Degradation | 1.5682 | 23.1479 | 24.2897 | 1.4533 | 13.9458
Module Number: BR33S3L3U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 29.2124 | 5.882 | 171.8269 | 35.8485 | 7.1403 | Cell performance is degraded or hotspot are formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 26.0173 | 5.4597 | 142.0458 | 32.581 | 6.6967
Difference | -0.2124 | 1.538 | 43.1731 | 0.1515 | 1.1597
Percentage Degradation | -0.7325 | 20.728 | 20.0805 | 0.421 | 13.9723

## Table 87
Module Number: BR33S5L4U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.4223 | 6.1718 | 175.4171 | 35.8539 | 7.0518 | Cell performance is degraded or hotspot are formed over the cells or low fill factor or snail trails are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.3381 | 5.7434 | 145.5268 | 32.6116 | 6.6302
Difference | 0.5777 | 1.2482 | 39.5829 | 0.1461 | 1.2482
Percentage Degradation | 1.9919 | 16.8221 | 18.4107 | 0.4059 | 15.0381
Module Number: BR33S7L3M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 18.3981 | 6.0751 | 111.7711 | 24.5443 | 7.2378 | Cell performance is degraded or one of the sub-string is open circuited or cells in sub- string burned or faulty bypass diode or snail trails formed on the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 16.8406 | 5.2253 | 87.9966 | 22.8128 | 6.2755
Difference | 10.6019 | 1.3449 | 103.2289 | 11.4557 | 1.0622
Percentage Degradation | 36.5582 | 18.1248 | 48.0135 | 31.8213 | 12.7972

## Table 88
Module Number: BR33S7L4M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 25.5329 | 5.64 | 144.0054 | 34.6579 | 7.4061 | Cell performance is degraded or hotspot are formed over the cells or low fill factor or snail trails are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 23.6427 | 4.9193 | 116.3054 | 32.5198 | 6.5052
Difference | 3.4671 | 1.78 | 70.9946 | 1.3421 | 0.8939
Percentage Degradation | 11.9553 | 23.9894 | 33.0207 | 3.7281 | 10.7704
Module Number: BR33S8L1M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.8927 | 6.1764 | 172.2761 | 34.7103 | 7.5171 | Cell performance is degraded or hotspot are formed over the cells or low fill factor or snail trails are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.7803 | 5.5434 | 142.9113 | 32.5198 | 6.7954
Difference | 1.1073 | 1.2436 | 42.7239 | 1.2897 | 0.7829
Percentage Degradation | 3.8184 | 16.7602 | 19.8716 | 3.5825 | 9.432

## Table 89
Module Number: BR33S9L1U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.3623 | 5.717 | 156.4299 | 34.517 | 7.4231 | Cell performance is degraded or hotspot are formed over the cells or low fill factor or snail trails are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.4332 | 5.0892 | 129.4357 | 32.4891 | 6.6523
Difference | 1.6377 | 1.703 | 58.5701 | 1.483 | 0.8769
Percentage Degradation | 5.6472 | 22.9517 | 27.2419 | 4.1194 | 10.5655
Module Number: BR33S9L1M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.0547 | 6.2046 | 174.0682 | 34.6395 | 7.5952 | Cell performance is degraded or hotspot are formed over the cells or low fill factor or snail trails are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.9945 | 5.4081 | 140.5811 | 32.5198 | 6.6665
Difference | 0.9453 | 1.2154 | 40.9318 | 1.3605 | 0.7048
Percentage Degradation | 3.2598 | 16.3799 | 19.0381 | 3.7792 | 8.492

## Table 90
Module Number: BR33S9L1L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.4638 | 6.3177 | 173.5075 | 34.7375 | 7.507 | Cell performance is degraded or hotspot are formed over the cells or low fill factor or snail trails are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.5631 | 5.5281 | 141.3154 | 32.7341 | 6.612
Difference | 1.5362 | 1.1023 | 41.4925 | 1.2625 | 0.793
Percentage Degradation | 5.2973 | 14.856 | 19.2988 | 3.5069 | 9.5548
Module Number: BR33S10L3M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.9914 | 6.1748 | 172.8403 | 34.5847 | 6.7343 | Cell performance is degraded or hotspot are formed over the cells or snail trails are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 26.1048 | 5.4236 | 141.5832 | 32.6422 | 5.9531
Difference | 1.0086 | 1.2452 | 42.1597 | 1.4153 | 1.5657
Percentage Degradation | 3.4778 | 16.7823 | 19.6092 | 3.9313 | 18.8643

## Table 91
Module Number: BR32S2L4U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 23.8591 | 6.9533 | 165.8989 | 34.3276 | 7.964 | Increased series resistance of module or low fill factor or hotspot formed over the cell.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 21.9171 | 6.6207 | 145.1059 | 31.9992 | 7.6418
Difference | 5.1409 | 0.4667 | 49.1011 | 1.6724 | 0.336
Percentage Degradation | 17.7272 | 6.2902 | 22.8377 | 4.6455 | 4.0483
Module Number: BR32S1L1M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 15.5243 | 6.5981 | 102.4302 | 33.7434 | 7.519 | Cell performance is degraded or one of the end of sub-string is open circuited or cells in sub-string burned or faulty bypass diode.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 14.2401 | 6.1884 | 88.1241 | 31.4174 | 7.1078
Difference | 13.4757 | 0.8219 | 112.5698 | 2.2566 | 0.781
Percentage Degradation | 46.4679 | 11.0774 | 52.3581 | 6.2682 | 9.4093

## Table 92
Module Number: BR31S5L3U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 25.6052 | 5.93 | 151.8381 | 34.0446 | 7.6448 | Cell performance is degraded or snail trails are formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 23.4275 | 5.5653 | 130.38 | 31.6317 | 7.2327
Difference | 3.3948 | 1.49 | 63.1619 | 1.9554 | 0.6552
Percentage Degradation | 11.7063 | 20.0812 | 29.3776 | 5.4317 | 7.8938
Module Number: BR30S10L2L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 24.411 | 6.1305 | 149.6513 | 33.0556 | 7.6371 | Cell performance is degraded or Increased series resistance of module or low fill factor or hotspot formed over the cell.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 22.8508 | 5.6614 | 129.3672 | 31.2949 | 7.0957
Difference | 4.589 | 1.2895 | 65.3487 | 2.9444 | 0.6629
Percentage Degradation | 15.8241 | 17.379 | 30.3947 | 8.179 | 7.9863

## Table 93
Module Number: BR30S8L3M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.6251 | 5.9599 | 158.684 | 34.051 | 8.1254 | Increased series resistance of module or low fill factor or hotspot formed over the cells or snail trails are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.4987 | 5.5644 | 136.3202 | 31.7848 | 7.6438
Difference | 2.3749 | 1.4601 | 56.316 | 1.949 | 0.1746
Percentage Degradation | 8.1893 | 19.6774 | 26.1935 | 5.4138 | 2.1032
Module Number: BR30S8L2M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.4002 | 6.7493 | 178.182 | 34.0776 | 8.2196 | Increased series resistance of module or low fill factor or hotspot formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.1549 | 6.1522 | 148.6053 | 31.6624 | 7.5532
Difference | 2.5998 | 0.6707 | 36.818 | 1.9224 | 0.0804
Percentage Degradation | 8.9649 | 9.0395 | 17.1247 | 5.34 | 0.9683

## Table 94
Module Number: BR29S8L1U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 25.6685 | 6.9178 | 177.5695 | 34.4893 | 8.3292 | Increased series resistance of module or low fill factor or hotspot formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 23.5539 | 6.1397 | 144.6151 | 32.1217 | 7.4504
Difference | 3.3315 | 0.5022 | 37.4305 | 1.5107 | -0.0292
Percentage Degradation | 11.4881 | 6.7681 | 17.4096 | 4.1963 | -0.3517
Module Number: BR29S9L1U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 25.0109 | 7.2743 | 181.9379 | 34.11 | 8.1922 | Low fill factor or hotspot formed over the cells or temperature variation within the cells at the backsheet of module.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 23.3153 | 6.7457 | 157.2773 | 32.1829 | 7.6459
Difference | 3.9891 | 0.1457 | 33.0621 | 1.89 | 0.1078
Percentage Degradation | 13.7555 | 1.963 | 15.3777 | 5.2499 | 1.2991

## Table 95
Module Number: BR29S10L2M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 25.282 | 7.2786 | 184.0166 | 34.098 | 8.0553 | Low fill factor or hotspot formed over the cells or temperature variation within the cells at the backsheet of module.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 23.4964 | 6.8226 | 160.307 | 32.0911 | 7.6015
Difference | 3.718 | 0.1414 | 30.9834 | 1.902 | 0.2447
Percentage Degradation | 12.8206 | 1.9062 | 14.4109 | 5.2834 | 2.9478
Module Number: BR29S10L3U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 25.2364 | 7.3452 | 185.3662 | 34.1977 | 8.1496 | Low fill factor or hotspot formed over the cells or temperature variation within the cells at the backsheet of module.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 23.4522 | 6.9335 | 162.6058 | 32.1829 | 7.7446
Difference | 3.7636 | 0.0748 | 29.6338 | 1.8023 | 0.1504
Percentage Degradation | 12.978 | 1.0081 | 13.7831 | 5.0064 | 1.812

## Table 96
Module Number: BR28S11L3M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.766 | 6.1352 | 170.3512 | 34.6503 | 7.1741 | Cell performance degraded or low fill factor or hotspot formed over the cells or snail trails are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.7762 | 5.8097 | 149.752 | 32.581 | 6.8398
Difference | 1.234 | 1.2848 | 44.6488 | 1.3497 | 1.1259
Percentage Degradation | 4.2551 | 17.3148 | 20.7669 | 3.7493 | 13.5654
Module Number: BR28S11L1L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.6455 | 6.156 | 164.0303 | 34.5929 | 7.0925 | Cell performance degraded or low fill factor or hotspot formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.6161 | 5.8817 | 144.7851 | 32.3973 | 6.8257
Difference | 2.3545 | 1.264 | 50.9697 | 1.4071 | 1.2075
Percentage Degradation | 8.119 | 17.0347 | 23.7068 | 3.9087 | 14.5479

## Table 97
Module Number: BR28S10L2L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.4811 | 5.9397 | 163.2301 | 34.5411 | 6.8097 | Cell performance degraded or hotspot formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.3759 | 5.6138 | 142.4564 | 32.336 | 6.4831
Difference | 1.5189 | 1.4803 | 51.7699 | 1.4589 | 1.4903
Percentage Degradation | 5.2374 | 19.95 | 24.079 | 4.0526 | 17.9553
Module Number: BR28S10L1U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.4661 | 6.1297 | 168.36 | 34.6801 | 6.8463 | Cell performance degraded or low fill factor or hotspot formed over the cells or snail trails are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.3547 | 5.7803 | 146.5571 | 32.4585 | 6.5032
Difference | 1.5339 | 1.2903 | 46.64 | 1.3199 | 1.4537
Percentage Degradation | 5.2893 | 17.389 | 21.693 | 3.6663 | 17.5148

## Table 98
Module Number: BR28S9L4L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.22 | 5.9845 | 162.8984 | 34.5132 | 6.9749 | Cell performance degraded or low fill factor or hotspot formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.2174 | 5.6337 | 142.0676 | 32.3973 | 6.612
Difference | 1.78 | 1.4355 | 52.1016 | 1.4868 | 1.3251
Percentage Degradation | 6.138 | 19.3461 | 24.2333 | 4.1301 | 15.965
Module Number: BR28S9L2U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.8751 | 5.5936 | 155.923 | 34.5852 | 6.9605 | Cell performance degraded or low fill factor or hotspot formed over the cells or snail trails are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.6109 | 5.2407 | 134.2189 | 32.2442 | 6.5717
Difference | 1.1249 | 1.8264 | 59.077 | 1.4148 | 1.3395
Percentage Degradation | 3.879 | 24.6141 | 27.4777 | 3.9299 | 16.1391

## Table 99
Module Number: BR28S8L2L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.99 | 5.988 | 161.6156 | 34.5797 | 6.824 | Cell performance degraded or low fill factor or hotspot formed over the cells or snail trails are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.9746 | 5.6258 | 140.5017 | 32.4279 | 6.4569
Difference | 2.01 | 1.432 | 53.3844 | 1.4203 | 1.476
Percentage Degradation | 6.9311 | 19.2994 | 24.8299 | 3.9454 | 17.7826
Module Number: BR28S7L4M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.4435 | 6.3263 | 173.6164 | 34.7486 | 7.2868 | Cell performance degraded or low fill factor or hotspot formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.4182 | 5.935 | 150.8559 | 32.6116 | 6.8841
Difference | 1.5565 | 1.0937 | 41.3836 | 1.2514 | 1.0132
Percentage Degradation | 5.3673 | 14.7396 | 19.2482 | 3.4761 | 12.2067

## Table 100
Module Number: BR28S7L3L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.2388 | 6.1109 | 166.4546 | 34.4694 | 6.9536 | Cell performance degraded or low fill factor or snail trails are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.1867 | 5.7043 | 143.673 | 32.3054 | 6.5375
Difference | 1.7612 | 1.3091 | 48.5454 | 1.5306 | 1.3464
Percentage Degradation | 6.0732 | 17.6423 | 22.5793 | 4.2516 | 16.2218
Module Number: BR28S6L1L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.1108 | 5.6057 | 151.9747 | 34.5073 | 6.0405 | Cell performance degraded or hotspot formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.8616 | 5.3625 | 133.3205 | 32.1217 | 5.8241
Difference | 1.8892 | 1.8143 | 63.0253 | 1.4927 | 2.2595
Percentage Degradation | 6.5146 | 24.4516 | 29.3141 | 4.1463 | 27.2232

## Table 101
Module Number: BR28S5L2L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 25.6182 | 7.4222 | 190.1426 | 34.3131 | 8.1053 | Low fill factor or snail trails are formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 23.9841 | 6.9628 | 166.9974 | 32.4891 | 7.6499
Difference | 3.3818 | -0.0022 | 24.8574 | 1.6869 | 0.1947
Percentage Degradation | 11.6613 | -0.0291 | 11.5616 | 4.6859 | 2.3457
Module Number: BR28S4L4L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.9232 | 6.7827 | 182.611 | 34.8387 | 7.8015 | Light cell performance degraded or hotspot formed on the cells or snail trails formed on the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.6591 | 6.5215 | 160.8148 | 32.3973 | 7.5612
Difference | 2.0768 | 0.6373 | 32.389 | 1.1613 | 0.4985
Percentage Degradation | 7.1614 | 8.5894 | 15.0647 | 3.2258 | 6.0057

## Table 102
Module Number: BR28S4L2M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.9371 | 5.5424 | 154.8391 | 34.5235 | 6.7173 | Cell performance degraded or hotspot formed on the cells or snail trails formed on the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.5453 | 5.2894 | 135.1192 | 32.0604 | 6.4629
Difference | 1.0629 | 1.8776 | 60.1609 | 1.4765 | 1.5827
Percentage Degradation | 3.6651 | 25.3044 | 27.9818 | 4.1013 | 19.0687
Module Number: BR28S1L4L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.6889 | 6.0744 | 168.1946 | 34.8981 | 7.018 | Cell performance degraded or hotspot formed on the cells or snail trails formed on the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.4245 | 5.9384 | 150.9812 | 32.5198 | 6.9143
Difference | 1.3111 | 1.3456 | 46.8054 | 1.1019 | 1.282
Percentage Degradation | 4.5209 | 18.1343 | 21.7699 | 3.0609 | 15.4452

## Table 103
Module Number: BR28S1L1U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 16.5969 | 5.4029 | 89.6719 | 28.1115 | 7.2622 | Cell performance is degraded or one of the end of sub-string is open circuited or cells in sub-string burned or faulty bypass diode.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 15.1859 | 5.3214 | 80.8107 | 26.1199 | 7.2106
Difference | 12.4031 | 2.0171 | 125.3281 | 7.8885 | 1.0378
Percentage Degradation | 42.7693 | 27.1843 | 58.2921 | 21.9124 | 12.5036
Module Number: BR27S5L1L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.2674 | 5.8998 | 160.8713 | 34.6823 | 6.8404 | Cell performance degraded or hotspot formed on the cells or snail trails formed on the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.0538 | 5.7177 | 143.2512 | 32.336 | 6.6806
Difference | 1.7326 | 1.5202 | 54.1287 | 1.3177 | 1.4596
Percentage Degradation | 5.9745 | 20.4883 | 25.1761 | 3.6603 | 17.5861

## Table 104
Module Number: BR27S5L2L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.056 | 4.4508 | 120.4203 | 34.4552 | 6.9998 | Cell performance degraded or hotspot formed on the cells or snail trails formed on the cells or low fill factor or burned cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.8571 | 4.2431 | 105.472 | 32.1217 | 6.7249
Difference | 1.944 | 2.9692 | 94.5797 | 1.5448 | 1.3002
Percentage Degradation | 6.7035 | 40.0164 | 43.9906 | 4.2911 | 15.665
Module Number: BR27S6L3L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 25.1587 | 5.0263 | 126.4546 | 34.1649 | 6.5771 | Cell performance degraded or hotspot formed on the cells or snail trails formed on the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 23.0285 | 4.7971 | 110.4707 | 31.7542 | 6.3279
Difference | 3.8413 | 2.3937 | 88.5454 | 1.8351 | 1.7229
Percentage Degradation | 13.2458 | 32.2605 | 41.1839 | 5.0975 | 20.7577

## Table 105
Module Number: BR27S7L4L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 21.6314 | 5.1554 | 111.5173 | 33.2817 | 7.0711 | Cell performance degraded or hotspot formed on the cells or snail trails formed on the cells or low fill factor or possible potential induced degradation.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 19.8668 | 4.9833 | 99.0015 | 31.0193 | 6.8881
Difference | 7.3686 | 2.2646 | 103.4827 | 2.7183 | 1.2289
Percentage Degradation | 25.4091 | 30.5208 | 48.1315 | 7.5508 | 14.8063
Module Number: BR26S11L1L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.6155 | 5.2044 | 148.9267 | 34.7783 | 5.8425 | Cell performance degraded or hotspot formed on the cells or snail trails formed on the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.8413 | 5.0623 | 130.8158 | 31.9686 | 5.7354
Difference | 0.3845 | 2.2156 | 66.0733 | 1.2217 | 2.4575
Percentage Degradation | 1.3258 | 29.8598 | 30.7318 | 3.3936 | 29.6086

## Table 106
Module Number: BR26S11L1M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.0186 | 6.0027 | 162.1846 | 34.8201 | 6.846 | Cell performance degraded or hotspot formed on the cells or snail trails formed on the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.6771 | 5.8728 | 144.9238 | 32.3054 | 6.7531
Difference | 1.9814 | 1.4173 | 52.8154 | 1.1799 | 1.454
Percentage Degradation | 6.8323 | 19.1011 | 24.5653 | 3.2774 | 17.5186
Module Number: BR26S11L2U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.657 | 5.8557 | 161.9508 | 34.8538 | 6.9245 | Cell performance degraded or burned cells or snail trails formed on the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.0262 | 5.7777 | 144.5946 | 32.0911 | 6.8942
Difference | 1.343 | 1.5643 | 53.0492 | 1.1462 | 1.3755
Percentage Degradation | 4.6311 | 21.0823 | 24.674 | 3.1838 | 16.5725

## Table 107
Module Number: BR26S10L1M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.2379 | 6.1723 | 174.2941 | 35.9596 | 6.7517 | Cell performance degraded or hotspot formed on the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.7944 | 6.0536 | 150.0947 | 32.3054 | 6.6987
Difference | 0.7621 | 1.2477 | 40.7059 | 0.0404 | 1.5483
Percentage Degradation | 2.6279 | 16.8147 | 18.933 | 0.1121 | 18.6539
Module Number: BR26S9L2U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.4612 | 6.168 | 169.3817 | 35.4418 | 6.7768 | Cell performance degraded or hotspot formed on the cells or snail trails formed on the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.4027 | 6.0239 | 146.9997 | 32.1523 | 6.6886
Difference | 1.5388 | 1.252 | 45.6183 | 0.5582 | 1.5232
Percentage Degradation | 5.3062 | 16.8728 | 21.2178 | 1.5506 | 18.3524

## Table 108
Module Number: BR26S8L4U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 18.2838 | 6.3863 | 116.7655 | 35.8135 | 7.2293 | Cell performance degraded or burned cells or snail trails formed on the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 16.1909 | 6.2552 | 101.2777 | 32.3973 | 7.1582
Difference | 10.7162 | 1.0337 | 98.2345 | 0.1865 | 1.0707
Percentage Degradation | 36.9524 | 13.9315 | 45.6905 | 0.518 | 12.8996
Module Number: BR26S7L1L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 24.8664 | 4.7377 | 117.8089 | 34.1537 | 7.9457 | Hotspot formed on the cells or burned cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 22.556 | 4.5344 | 102.2781 | 31.5093 | 7.6721
Difference | 4.1336 | 2.6823 | 97.1911 | 1.8463 | 0.3543
Percentage Degradation | 14.2538 | 36.15 | 45.2052 | 5.1287 | 4.2689

## Table 109
Module Number: BR26S6L3U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 25.7913 | 5.2335 | 134.98 | 35.1654 | 6.9345 | Cell performance degraded or hotspot formed on the cells or snail trails formed on thr cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 23.2203 | 5.0412 | 117.0571 | 32.2442 | 6.743
Difference | 3.2087 | 2.1865 | 80.02 | 0.8346 | 1.3655
Percentage Degradation | 11.0644 | 29.467 | 37.2186 | 2.3184 | 16.4513
Module Number: BR26S5L3L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 25.1754 | 5.526 | 139.118 | 34.3826 | 6.6646 | Cell performance degraded or hotspot formed on the cells or snail trails formed on thr cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 22.9466 | 5.3106 | 121.8615 | 31.8461 | 6.4589
Difference | 3.8246 | 1.894 | 75.882 | 1.6174 | 1.6354
Percentage Degradation | 13.1884 | 25.5262 | 35.294 | 4.4927 | 19.7042

## Table 110
Module Number: BR26S4L3U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 15.9283 | 7.7858 | 124.0145 | 35.9069 | 8.5638 | Burned cells or small hole observed at the backsheet of module or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 14.223 | 7.4361 | 105.7636 | 32.7035 | 8.2625
Difference | 13.0717 | -0.3658 | 90.9855 | 0.0931 | -0.2638
Percentage Degradation | 45.0749 | -4.93 | 42.3189 | 0.2587 | -3.1785
Module Number: BR26S2L4U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.6128 | 5.449 | 145.0122 | 35.8632 | 8.3433 | Hotspot formed on the cells or snail trails formed on thr cells or low fill factor or bubbles are formed at the backsheet of module.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 23.7719 | 5.0931 | 121.0716 | 32.6729 | 7.8776
Difference | 2.3872 | 1.971 | 69.9878 | 0.1368 | -0.0433
Percentage Degradation | 8.2316 | 26.5639 | 32.5525 | 0.38 | -0.5215

## Table 111
Module Number: BR26S1L4U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.6707 | 6.425 | 177.7836 | 35.8793 | 7.9552 | Hotspot formed on the cells or snail trails formed on thr cells or low fill factor or burned cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.5615 | 6.0566 | 148.76 | 32.5198 | 7.5794
Difference | 1.3293 | 0.995 | 37.2164 | 0.1207 | 0.3448
Percentage Degradation | 4.5839 | 13.4099 | 17.3099 | 0.3352 | 4.1542
Module Number: BR26S1L2M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.7576 | 6.2123 | 178.6496 | 35.9278 | 7.828 | Light cell performance degraded or hotspot formed on the cells or snail trails formed on thr cells or low fill factor or burned cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.5135 | 5.9969 | 153.0026 | 32.5504 | 7.6378
Difference | 0.2424 | 1.2077 | 36.3504 | 0.0722 | 0.472
Percentage Degradation | 0.8358 | 16.2769 | 16.9072 | 0.2005 | 5.6873

## Table 112
Module Number: BR25S1L2L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.7371 | 5.5343 | 147.9697 | 33.8188 | 7.7897 | Light cell performance degraded or bubbles are formed at the backsheet of module or low fill factor or burned cells or temperature variation within the cells of module.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.2555 | 5.3547 | 129.8803 | 31.203 | 7.6035
Difference | 2.2629 | 1.8857 | 67.0303 | 2.1812 | 0.5103
Percentage Degradation | 7.8032 | 25.4144 | 31.1769 | 6.059 | 6.1484
Module Number: BR25S1L4U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 25.9684 | 6.4033 | 166.2828 | 34.0054 | 7.909 | Light cell performance degraded or hotspot formed on the cells or bubbles are formed at the backsheet of module or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 23.4845 | 6.1133 | 143.5686 | 31.2949 | 7.6197
Difference | 3.0316 | 1.0167 | 48.7172 | 1.9946 | 0.391
Percentage Degradation | 10.4538 | 13.7025 | 22.6592 | 5.5405 | 4.7107

## Table 113
Module Number: BR25S9L2U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.0812 | 5.8502 | 164.2817 | 34.6358 | 7.3479 | Cell performance degraded or hotspot formed on the cells or low fill factor or burned cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.7842 | 5.6615 | 145.9771 | 32.2748 | 7.1662
Difference | 0.9188 | 1.5698 | 50.7183 | 1.3642 | 0.9521
Percentage Degradation | 3.1683 | 21.1558 | 23.5899 | 3.7896 | 11.4711
Module Number: BR25S9L3U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.9249 | 5.7665 | 155.2613 | 34.617 | 7.323 | Cell performance degraded or hotspot formed on the cells or low fill factor or burned cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.7102 | 5.5535 | 137.2282 | 32.2442 | 7.1078
Difference | 2.0751 | 1.6535 | 59.7387 | 1.383 | 0.977
Percentage Degradation | 7.1557 | 22.2848 | 27.7855 | 3.8418 | 11.7712

## Table 114
Module Number: BR25S10L4M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.2819 | 5.8687 | 154.2402 | 34.0089 | 6.7718 | Cell performance degraded or hotspot formed on the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.4182 | 5.6155 | 137.1194 | 31.9992 | 6.5234
Difference | 2.7181 | 1.5513 | 60.7598 | 1.9911 | 1.5282
Percentage Degradation | 9.3729 | 20.9071 | 28.2604 | 5.5308 | 18.4121
Module Number: BR25S11L1L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 16.1094 | 6.4719 | 104.2589 | 33.0843 | 7.2267 | Cell performance is degraded or one of the end of sub-string is open circuited or cells in sub-string burned or faulty bypass diode.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 15.0281 | 6.0937 | 91.576 | 31.2337 | 6.8478
Difference | 12.8906 | 0.9481 | 110.7411 | 2.9157 | 1.0733
Percentage Degradation | 44.4504 | 12.7772 | 51.5075 | 8.0992 | 12.9313

## Table 115
Module Number: BR25S11L4U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 23.7759 | 4.5884 | 109.0937 | 33.95 | 6.9489 | Cell performance degraded or hotspot formed on the cells or low fill factor or burned cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 22.0593 | 4.3124 | 95.128 | 31.9073 | 6.5758
Difference | 5.2241 | 2.8316 | 105.9063 | 2.05 | 1.3511
Percentage Degradation | 18.014 | 38.1616 | 49.2587 | 5.6945 | 16.2783
Module Number: BR25S11L4L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 17.0991 | 6.1662 | 105.4364 | 34.3382 | 6.7259 | Cell performance is degraded or one of the end of sub-string is open circuited or cells in sub-string burned or faulty bypass diode.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 15.8112 | 5.8792 | 92.9574 | 32.1829 | 6.4589
Difference | 11.9009 | 1.2538 | 109.5636 | 1.6618 | 1.5741
Percentage Degradation | 41.0375 | 16.8977 | 50.9598 | 4.6161 | 18.9648

## Table 116
Module Number: BR24S12L1U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.7219 | 6.8033 | 181.798 | 34.4962 | 8.0992 | Hotspot formed over the cells or snail trails are formed on the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.4008 | 6.5193 | 159.0754 | 31.9992 | 7.8252
Difference | 2.2781 | 0.6167 | 33.202 | 1.5038 | 0.2008
Percentage Degradation | 7.8555 | 8.3109 | 15.4428 | 4.1771 | 2.4197
Module Number: BR25S6L1L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.1984 | 6.3441 | 166.2037 | 33.7543 | 7.7795 | Cell performance is degraded or hotspot formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.1074 | 6.0494 | 145.8362 | 31.5093 | 7.4746
Difference | 2.8016 | 1.0759 | 48.7963 | 2.2457 | 0.5205
Percentage Degradation | 9.6609 | 14.5006 | 22.696 | 6.2382 | 6.2717

## Table 117
Module Number: BR24S5L2U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.5582 | 5.9227 | 157.2959 | 34.0068 | 7.8073 | Increased shunt and series resistance or hotspot formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.1888 | 5.6938 | 137.7258 | 31.4786 | 7.5693
Difference | 2.4418 | 1.4973 | 57.7041 | 1.9932 | 0.4927
Percentage Degradation | 8.4201 | 20.1794 | 26.8391 | 5.5366 | 5.9365
Module Number: BR24S3L2L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 18.3115 | 5.3941 | 98.7737 | 33.2844 | 7.5328 | Cell performance is degraded or hotspot formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 16.9577 | 5.2447 | 88.9382 | 31.2337 | 7.3758
Difference | 10.6885 | 2.0259 | 116.2263 | 2.7156 | 0.7672
Percentage Degradation | 36.8567 | 27.3037 | 54.0588 | 7.5434 | 9.2431

## Table 118
Module Number: BR23S1L1U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 23.7463 | 6.6854 | 158.7543 | 34.6002 | 8.7005 | Increased series resistance or hotspot formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 21.9824 | 6.5811 | 144.6689 | 32.4585 | 8.6253
Difference | 5.2537 | 0.7346 | 56.2457 | 1.3998 | -0.4005
Percentage Degradation | 18.1163 | 9.8997 | 26.1608 | 3.8884 | -4.8249
Module Number: BR23S1L4L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.6888 | 6.2264 | 166.176 | 34.2321 | 7.111 | Cell performance is degraded or snail trails are formed over the cells or low fill factor or hotspot formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.8289 | 6.1125 | 151.766 | 32.2442 | 7.0272
Difference | 2.3112 | 1.1936 | 48.824 | 1.7679 | 1.189
Percentage Degradation | 7.9697 | 16.0858 | 22.7088 | 4.9108 | 14.3252

## Table 119
Module Number: BR23S2L3L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.9676 | 5.6828 | 158.9357 | 34.4296 | 7.0294 | Cell performance is degraded or snail trails are formed over the cells or low fill factor or hotspot formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.897 | 5.6024 | 145.0867 | 32.3054 | 6.9788
Difference | 1.0324 | 1.7372 | 56.0643 | 1.5704 | 1.2706
Percentage Degradation | 3.5599 | 23.4118 | 26.0764 | 4.3623 | 15.3084
Module Number: BR23S2L4U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.6221 | 5.8224 | 155.0047 | 34.071 | 6.5471 | Cell performance is degraded or snail trails are formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.7943 | 5.6764 | 140.7418 | 32.1217 | 6.4246
Difference | 2.3779 | 1.5976 | 59.9953 | 1.929 | 1.7529
Percentage Degradation | 8.1998 | 21.5308 | 27.9048 | 5.3582 | 21.1194

## Table 120
Module Number: BR23S2L4M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.1326 | 6.8765 | 179.7001 | 34.8121 | 7.7011 | Light cell performance is degraded or low fill factor or hotspot formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.0952 | 6.6786 | 160.9214 | 32.5504 | 7.535
Difference | 2.8674 | 0.5435 | 35.2999 | 1.1879 | 0.5989
Percentage Degradation | 9.8877 | 7.325 | 16.4186 | 3.2999 | 7.2151
Module Number: BR23S3L1M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.2895 | 6.3256 | 166.2972 | 34.4583 | 7.3042 | Cell performance is degraded or snail trails are formed over the cells or low fill factor or hotspot formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.3184 | 6.0946 | 148.2108 | 32.3054 | 7.0876
Difference | 2.7105 | 1.0944 | 48.7028 | 1.5417 | 0.9958
Percentage Degradation | 9.3467 | 14.749 | 22.6525 | 4.2824 | 11.9981

## Table 121
Module Number: BR23S6L2M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.1517 | 5.4303 | 147.4418 | 34.0148 | 5.9281 | Cell performance is degraded or hotspot formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.3383 | 5.1894 | 131.4894 | 32.1217 | 5.7011
Difference | 1.8483 | 1.9897 | 67.5582 | 1.9852 | 2.3719
Percentage Degradation | 6.3734 | 26.8154 | 31.4224 | 5.5143 | 28.5766
Module Number: BR23S8L2M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.139 | 5.9054 | 160.2663 | 34.2432 | 6.6545 | Cell performance is degraded or snail trails are formed over the cells or hotspot formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.3543 | 5.7512 | 145.8185 | 32.3666 | 6.5214
Difference | 1.861 | 1.5146 | 54.7337 | 1.7568 | 1.6455
Percentage Degradation | 6.4172 | 20.4126 | 25.4575 | 4.8801 | 19.8255

## Table 122
Module Number: BR23S8L4U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.0458 | 5.6186 | 157.5774 | 34.4929 | 6.8975 | Cell performance is degraded or low fill factor or hotspot formed over the cells or burned cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 26.0609 | 5.5147 | 143.7171 | 32.4585 | 6.8156
Difference | 0.9542 | 1.8014 | 57.4226 | 1.5071 | 1.4025
Percentage Degradation | 3.2903 | 24.2781 | 26.7082 | 4.1865 | 16.8976
Module Number: BR23S9L3L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 17.1373 | 6.071 | 104.0406 | 34.2121 | 6.6491 | Cell performance is degraded or one of the end of sub-string is open circuited or cells in sub-string burned or faulty bypass diode.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 15.8808 | 5.9916 | 95.1519 | 32.1217 | 6.608
Difference | 11.8627 | 1.349 | 110.9594 | 1.7879 | 1.6509
Percentage Degradation | 40.9058 | 18.1806 | 51.609 | 4.9665 | 19.8903

## Table 123
Module Number: BR23S9L4L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.1887 | 5.9298 | 161.2228 | 34.6032 | 6.6221 | Cell performance is degraded or hotspot formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.9644 | 5.8624 | 146.352 | 32.2442 | 6.5979
Difference | 1.8113 | 1.4902 | 53.7772 | 1.3968 | 1.6779
Percentage Degradation | 6.2459 | 20.0839 | 25.0127 | 3.8801 | 20.2151
Module Number: BR23S10L3M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.2328 | 5.5237 | 150.4262 | 34.1172 | 6.7727 | Cell performance is degraded or low fill factor or hotspot formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.2627 | 5.4521 | 137.7339 | 32.0604 | 6.7309
Difference | 1.7672 | 1.8963 | 64.5738 | 1.8828 | 1.5273
Percentage Degradation | 6.0939 | 25.5563 | 30.0343 | 5.23 | 18.4008

## Table 124
Module Number: BR23S11L2M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 22.3192 | 6.8039 | 151.8589 | 34.2743 | 8.4418 | Increased series resistance of the cells or hotspot formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 20.8046 | 6.7361 | 140.1417 | 32.336 | 8.4117
Difference | 6.6808 | 0.6161 | 63.1411 | 1.7257 | -0.1418
Percentage Degradation | 23.0372 | 8.3026 | 29.368 | 4.7936 | -1.7088
Module Number: BR23S12L3L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 23.3269 | 5.6179 | 131.049 | 34.0007 | 8.112 | Increased series resistance of the cells or hotspot formed over the cells or low fill factor or bubbles are form at thr backsheet of the module.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 21.7295 | 5.5339 | 120.2498 | 32.0604 | 8.0429
Difference | 5.6731 | 1.8021 | 83.951 | 1.9993 | 0.188
Percentage Degradation | 19.5626 | 24.2865 | 39.047 | 5.5537 | 2.2645

## Table 125
Module Number: BR23S12L1U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 23.4141 | 7.4221 | 173.7817 | 35.7737 | 8.5549 | Increased series resistance of the cells or hotspot formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 21.2192 | 7.3511 | 155.9846 | 32.9791 | 8.5487
Difference | 5.5859 | -0.0021 | 41.2183 | 0.2263 | -0.2549
Percentage Degradation | 19.2617 | -0.0282 | 19.1713 | 0.6285 | -3.0706
Module Number: BR22S12L1L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.0894 | 6.5531 | 170.9673 | 34.6855 | 7.1637 | Cell performance is degraded or hotspot formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.0793 | 6.4546 | 155.4224 | 32.4585 | 7.1078
Difference | 2.9106 | 0.8669 | 44.0327 | 1.3145 | 1.1363
Percentage Degradation | 10.0366 | 11.6827 | 20.4803 | 3.6514 | 13.69

## Table 126
Module Number: BR22S12L1M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.7611 | 5.8958 | 157.7781 | 34.4236 | 6.4056 | Cell performance is degraded or snail trails formed over the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.5851 | 5.8348 | 143.4483 | 32.0911 | 6.3883
Difference | 2.2389 | 1.5242 | 57.2219 | 1.5764 | 1.8944
Percentage Degradation | 7.7203 | 20.5418 | 26.6148 | 4.3789 | 22.8245
Module Number: BR22S11L4L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.4714 | 5.9836 | 158.3933 | 34.2842 | 6.6461 | Cell performance is degraded or snail trails formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.3542 | 5.8179 | 141.6896 | 31.9992 | 6.5113
Difference | 2.5286 | 1.4364 | 56.6067 | 1.7158 | 1.6539
Percentage Degradation | 8.7194 | 19.3589 | 26.3287 | 4.766 | 19.9265

## Table 127
Module Number: BR22S11L3L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.529 | 5.9198 | 157.046 | 34.1613 | 6.6447 | Cell performance is degraded or snail trails formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.5142 | 5.745 | 140.8334 | 31.9992 | 6.4952
Difference | 2.471 | 1.5002 | 57.954 | 1.8387 | 1.6553
Percentage Degradation | 8.5207 | 20.2185 | 26.9554 | 5.1076 | 19.943
Module Number: BR22S11L2U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.7195 | 5.6251 | 150.2987 | 33.942 | 6.6097 | Cell performance is degraded or hotspot formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.7685 | 5.4622 | 135.2893 | 31.8767 | 6.4629
Difference | 2.2805 | 1.7949 | 64.7013 | 2.058 | 1.6903
Percentage Degradation | 7.8638 | 24.1906 | 30.0936 | 5.7165 | 20.3652

## Table 128
Module Number: BR22S10L2L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.1912 | 5.9263 | 155.2181 | 34.9022 | 8.1934 | Hotspot formed on the cells or low fill factor or bubbles are formed at the backsheet of the module.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.1285 | 5.7409 | 138.5181 | 32.6116 | 7.9965
Difference | 2.8088 | 1.4937 | 59.7819 | 1.0978 | 0.1066
Percentage Degradation | 9.6855 | 20.1301 | 27.8055 | 3.0493 | 1.2839
Module Number: BR22S9L1L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.5655 | 5.6458 | 149.9824 | 34.0091 | 6.5083 | Cell performance is degraded or hotspot formed over the cells or low fill factor or temperature variation within the cells of module.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.7103 | 5.4999 | 135.9033 | 32.0298 | 6.3823
Difference | 2.4345 | 1.7742 | 65.0176 | 1.9909 | 1.7917
Percentage Degradation | 8.3947 | 23.9117 | 30.2408 | 5.5304 | 21.5868

## Table 129
Module Number: BR22S8L4U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 13.8396 | 6.3674 | 88.1224 | 25.9835 | 8.3803 | One of the end of sub-string is open circuited or cells in sub-string burned or faulty bypass diode.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 12.6938 | 6.2622 | 79.4917 | 24.1908 | 8.3069
Difference | 15.1604 | 1.0526 | 126.8776 | 10.0165 | -0.0803
Percentage Degradation | 52.2771 | 14.1861 | 59.0128 | 27.8236 | -0.967
Module Number: BR22S8L1U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.5993 | 5.3794 | 143.0874 | 35.1595 | 8.1496 | Hotspot formed on the cells or low fill factor or bubbles are formed at the backsheet of the module.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.2584 | 5.2846 | 128.195 | 32.581 | 8.0731
Difference | 2.4007 | 2.0406 | 71.9126 | 0.8405 | 0.1504
Percentage Degradation | 8.2782 | 27.5018 | 33.4477 | 2.3347 | 1.8116

## Table 130
Module Number: BR22S7L1L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 19.0468 | 4.0451 | 77.0456 | 32.5016 | 6.2931 | Cell performance is degraded or hotspot formed on the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 17.5522 | 3.8817 | 68.132 | 30.3763 | 6.084
Difference | 9.9532 | 3.3749 | 137.9544 | 3.4984 | 2.0069
Percentage Degradation | 34.3214 | 45.4842 | 64.1648 | 9.7179 | 24.1794
Module Number: BR22S6L1M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 25.5934 | 5.8129 | 148.7722 | 34.7158 | 7.4273 | Cell performance is degraded or hotspot formed on the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 23.4069 | 5.1112 | 119.6374 | 32.2442 | 6.5838
Difference | 3.4066 | 1.6071 | 66.2278 | 1.2842 | 0.8727
Percentage Degradation | 11.7468 | 21.659 | 30.8036 | 3.5673 | 10.5149

## Table 131
Module Number: BR22S5L3U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.3279 | 5.4266 | 142.8714 | 33.8411 | 6.0667 | Cell performance is degraded or hotspot formed on the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.7226 | 5.115 | 126.457 | 32.1217 | 5.7515
Difference | 2.6721 | 1.9934 | 72.1286 | 2.1589 | 2.2333
Percentage Degradation | 9.2143 | 26.8649 | 33.5482 | 5.9968 | 26.9077
Module Number: BR22S4L1U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 25.9296 | 7.2976 | 189.2251 | 34.425 | 8.0563 | Good Module
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.1799 | 6.878 | 166.3092 | 32.4891 | 7.6418
Difference | 3.0704 | 0.1224 | 25.7749 | 1.575 | 0.2437
Percentage Degradation | 10.5875 | 1.6491 | 11.9883 | 4.375 | 2.9361

## Table 132
Module Number: BR22S2L4L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.6827 | 5.6146 | 149.8124 | 33.7204 | 6.0869 | Cell performance is degraded or hotspot formed on the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.9029 | 5.3235 | 132.5699 | 31.8461 | 5.808
Difference | 2.3173 | 1.8054 | 65.1876 | 2.2796 | 2.2131
Percentage Degradation | 7.9909 | 24.3315 | 30.3198 | 6.3321 | 26.6638
Module Number: BR22S2L4U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.695 | 5.9346 | 164.3597 | 34.6667 | 7.0322 | Cell performance is degraded or hotspot formed on the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.4901 | 5.7389 | 146.2853 | 32.3666 | 6.8519
Difference | 1.305 | 1.4854 | 50.6403 | 1.3333 | 1.2678
Percentage Degradation | 4.5 | 20.0184 | 23.5536 | 3.7037 | 15.2746

## Table 133
Module Number: BR21S1L1M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 25.9075 | 5.501 | 142.5169 | 33.0437 | 8.0078 | Increased shunt and series resistance or hotspot formed over the cells or low fill factor or possible potential induced degradation.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.0604 | 5.0231 | 120.8568 | 31.0806 | 7.3617
Difference | 3.0925 | 1.919 | 72.4831 | 2.9563 | 0.2922
Percentage Degradation | 10.6638 | 25.8627 | 33.7131 | 8.2118 | 3.5204
Module Number: BR21S1L1L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.5632 | 6.087 | 161.6902 | 34.0603 | 7.8888 | Increased shunt and series resistance or hotspot formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.2044 | 5.5756 | 134.955 | 31.5399 | 7.2872
Difference | 2.4368 | 1.333 | 53.3098 | 1.9397 | 0.4112
Percentage Degradation | 8.4027 | 17.965 | 24.7952 | 5.3881 | 4.9545

## Table 134
Module Number: BR21S10L1M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 25.9344 | 5.9111 | 153.2997 | 33.5837 | 7.6479 | Cell performance is degraded or hotspot formed over the cells or low fill factor or possible potential induced degradation.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.2958 | 5.6899 | 138.2398 | 31.8155 | 7.406
Difference | 3.0656 | 1.5089 | 61.7003 | 2.4163 | 0.6521
Percentage Degradation | 10.5711 | 20.3361 | 28.6978 | 6.7118 | 7.8562
Module Number: BR21S11L2M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.2671 | 5.5493 | 145.7649 | 33.4952 | 7.5509 | Cell performance is degraded or hotspot formed over the cells or low fill factor or burned cells or possible potential induced degradation.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.6864 | 5.347 | 131.9991 | 31.8155 | 7.3174
Difference | 2.7329 | 1.8707 | 69.2351 | 2.5048 | 0.7491
Percentage Degradation | 9.424 | 25.211 | 32.2024 | 6.9578 | 9.0247

## Table 135
Module Number: BR21S12L2M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.0114 | 5.1301 | 133.441 | 33.7016 | 7.6507 | Cell performance is degraded or hotspot formed over the cells or low fill factor or possible potential induced degradation.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.463 | 4.9528 | 121.1615 | 32.0298 | 7.4282
Difference | 2.9886 | 2.2899 | 81.559 | 2.2984 | 0.6493
Percentage Degradation | 10.3055 | 30.8612 | 37.9344 | 6.3844 | 7.823
Module Number: BR20S12L3U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.9168 | 4.9687 | 138.709 | 34.4289 | 7.1182 | Cell performance is degraded or hotspot formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 26.089 | 4.7769 | 124.6236 | 32.5504 | 6.8861
Difference | 1.0832 | 2.4513 | 76.291 | 1.5711 | 1.1818
Percentage Degradation | 3.7352 | 33.037 | 35.4842 | 4.3643 | 14.2385

## Table 136
Module Number: BR20S12L1L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 25.5053 | 5.9547 | 151.8755 | 33.8856 | 6.9395 | Cell performance is degraded or hotspot formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.2163 | 5.7102 | 138.2799 | 32.4585 | 6.6866
Difference | 3.4947 | 1.4653 | 63.1245 | 2.1144 | 1.3605
Percentage Degradation | 12.0508 | 19.7484 | 29.3602 | 5.8735 | 16.3917
Module Number: BR20S11L2M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.1453 | 5.4885 | 148.9874 | 33.7534 | 6.8407 | Cell performance is degraded or hotspot formed over the cells or low fill factor or possible potential induced degradation.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.7479 | 5.247 | 135.0996 | 32.3054 | 6.5717
Difference | 1.8547 | 1.9315 | 66.0126 | 2.2466 | 1.4593
Percentage Degradation | 6.3955 | 26.0308 | 30.7035 | 6.2407 | 17.5822

## Table 137
Module Number: BR20S10L4U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.7928 | 5.6356 | 156.6287 | 35.0542 | 8.5036 | Hotspot formed over the cells or burned cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.7311 | 5.4149 | 139.3299 | 32.8872 | 8.2283
Difference | 1.2072 | 1.7844 | 58.3713 | 0.9458 | -0.2036
Percentage Degradation | 4.1628 | 24.0487 | 27.1494 | 2.6272 | -2.4532
Module Number: BR20S10L2M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 16.1072 | 5.8653 | 94.4738 | 24.2765 | 8.223 | One of the sub-string is open circuited or cells in sub-string burned or faulty bypass diode.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 15.1125 | 5.6719 | 85.7164 | 23.0272 | 7.9985
Difference | 12.8928 | 1.5547 | 120.5262 | 11.7235 | 0.077
Percentage Degradation | 44.4578 | 20.9528 | 56.0587 | 32.5653 | 0.9283

## Table 138
Module Number: BR20S10L2L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.8729 | 6.0317 | 162.0896 | 34.5689 | 8.0611 | Hotspot formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.1613 | 5.8124 | 146.2481 | 32.7341 | 7.8151
Difference | 2.1271 | 1.3883 | 52.9104 | 1.4311 | 0.2389
Percentage Degradation | 7.3349 | 18.71 | 24.6095 | 3.9753 | 2.8782
Module Number: BR20S8L2M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.2946 | 5.0996 | 134.0915 | 33.6218 | 6.8427 | Cell performance is degraded or hotspot formed over the cells or low fill factor or cell temperature variation within cells of module.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.0305 | 4.9007 | 122.6679 | 32.2748 | 6.606
Difference | 2.7054 | 2.3204 | 80.9085 | 2.3782 | 1.4573
Percentage Degradation | 9.3288 | 31.2726 | 37.6318 | 6.606 | 17.5581

## Table 139
Module Number: BR20S8L1M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 25.9573 | 6.4557 | 167.571 | 33.9753 | 7.682 | Cell performance is degraded or hotspot formed over the cells or low fill factor or cell temperature variation within cells of module.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.8474 | 6.1918 | 153.8502 | 32.7647 | 7.398
Difference | 3.0427 | 0.9643 | 47.429 | 2.0247 | 0.618
Percentage Degradation | 10.4922 | 12.9966 | 22.06 | 5.6242 | 7.4463
Module Number: BR20S7L2U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.2274 | 5.6835 | 149.0645 | 33.5434 | 7.0055 | Cell performance is degraded or hotspot formed over the cells or low fill factor or cell temperature variation within cells of module.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.9797 | 5.4443 | 135.9968 | 32.2135 | 6.741
Difference | 2.7726 | 1.7365 | 65.9355 | 2.4566 | 1.2945
Percentage Degradation | 9.5606 | 23.4024 | 30.6677 | 6.824 | 15.5965

## Table 140
Module Number: BR20S6L3U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.8953 | 5.5995 | 156.1997 | 34.2375 | 6.8869 | Cell performance is degraded or hotspot formed over the cells or low fill factor or cell temperature variation within cells of module.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.7668 | 5.2396 | 135.0079 | 32.0604 | 6.4911
Difference | 1.1047 | 1.8205 | 58.8003 | 1.7625 | 1.4131
Percentage Degradation | 3.8093 | 24.5351 | 27.349 | 4.896 | 17.025
Module Number: BR20S6L2U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.0927 | 5.9251 | 166.4528 | 34.505 | 7.38 | Cell performance is degraded or hotspot formed over the cells or low fill factor or cell temperature variation within cells of module.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.854 | 5.4613 | 141.1959 | 32.2135 | 6.8539
Difference | 0.9073 | 1.4949 | 48.5472 | 1.495 | 0.92
Percentage Degradation | 3.1286 | 20.1466 | 22.5801 | 4.1529 | 11.0845

## Table 141
Module Number: BR20S6L1L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.3468 | 5.8779 | 160.7406 | 33.9845 | 7.3919 | Cell performance is degraded or hotspot formed over the cells or low fill factor or cell temperature variation within cells of module.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.6071 | 5.4379 | 139.249 | 32.1829 | 6.8801
Difference | 1.6532 | 1.5421 | 54.2594 | 2.0155 | 0.9081
Percentage Degradation | 5.7008 | 20.7835 | 25.2369 | 5.5987 | 10.9405
Module Number: BR20S5L3L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.6281 | 5.8936 | 156.9343 | 34.0152 | 6.287 | Cell performance is degraded or hotspot formed over the cells or cell temperature variation within cells of module.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.7343 | 5.5542 | 137.3795 | 31.9992 | 5.9651
Difference | 2.3719 | 1.5264 | 58.0657 | 1.9848 | 2.013
Percentage Degradation | 8.179 | 20.572 | 27.0073 | 5.5133 | 24.2529

## Table 142
Module Number: BR20S3L4L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.7328 | 5.7045 | 152.4973 | 33.9727 | 6.798 | Cell performance is degraded or hotspot formed over the cells or low fill factor or cell temperature variation within cells of module.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.956 | 5.3254 | 132.9003 | 32.0911 | 6.3863
Difference | 2.2672 | 1.7155 | 62.5027 | 2.0273 | 1.502
Percentage Degradation | 7.8179 | 23.12 | 29.071 | 5.6314 | 18.097
Module Number: BR20S3L4M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.4421 | 3.948 | 104.3938 | 34.0465 | 6.9885 | Cell performance is degraded or hotspot formed over the cells or low fill factor or cell temperature variation within cells of module.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.5911 | 3.697 | 90.9138 | 32.0604 | 6.5879
Difference | 2.5579 | 3.472 | 110.6062 | 1.9535 | 1.3115
Percentage Degradation | 8.8204 | 46.7922 | 51.4447 | 5.4264 | 15.8007

## Table 143
Module Number: BR20S1L4L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.1113 | 5.486 | 143.2465 | 33.8704 | 7.4957 | Cell performance is degraded or hotspot formed over the cells or low fill factor or cell temperature variation within cells of module.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.2952 | 5.1005 | 123.9177 | 31.9073 | 7.0151
Difference | 2.8887 | 1.934 | 71.7535 | 2.1296 | 0.8043
Percentage Degradation | 9.9611 | 26.0646 | 33.3737 | 5.9155 | 9.691
Module Number: BR20S1L3M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.4925 | 5.608 | 154.1795 | 34.1317 | 7.195 | Cell performance is degraded or hotspot formed over the cells or low fill factor or cell temperature variation within cells of module.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.4609 | 5.2097 | 132.6431 | 32.0298 | 6.7309
Difference | 1.5075 | 1.812 | 60.8205 | 1.8683 | 1.105
Percentage Degradation | 5.1981 | 24.4198 | 28.2886 | 5.1897 | 13.3133

## Table 144
Module Number: BR20S1L1U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 17.8776 | 5.907 | 105.6031 | 23.2709 | 6.9001 | One of the sub-string is open circuited or cells in sub-string burned or faulty bypass diode.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 16.1849 | 5.5072 | 89.1338 | 21.4349 | 6.4911
Difference | 11.1224 | 1.513 | 109.3969 | 12.7291 | 1.3999
Percentage Degradation | 38.3533 | 20.3905 | 50.8823 | 35.3585 | 16.8657
Module Number: BR19S1L2M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.4854 | 6.3954 | 175.7796 | 34.57 | 7.4329 | Cell performance is degraded or hotspot is formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.1203 | 5.4021 | 135.7021 | 32.0911 | 6.3299
Difference | 1.5146 | 1.0246 | 39.2204 | 1.43 | 0.8671
Percentage Degradation | 5.2226 | 13.809 | 18.242 | 3.9722 | 10.4473

## Table 145
Module Number: BR19S1L2L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.1825 | 6.1841 | 161.916 | 34.1048 | 7.3619 | Cell performance is degraded or hotspot is formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.2991 | 5.1449 | 125.0161 | 32.0604 | 6.1667
Difference | 2.8175 | 1.2359 | 53.084 | 1.8952 | 0.9381
Percentage Degradation | 9.7156 | 16.6559 | 24.6902 | 5.2645 | 11.3025
Module Number: BR19S2L4L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 14.2344 | 6.2084 | 88.3724 | 32.4193 | 7.3057 | One of the end of sub-string is open circuited or cells in sub-string burned or faulty bypass diode.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 13.2386 | 5.0968 | 67.475 | 30.5294 | 6.0377
Difference | 14.7656 | 1.2116 | 126.6276 | 3.5807 | 0.9943
Percentage Degradation | 50.9158 | 16.3293 | 58.8965 | 9.9463 | 11.979

## Table 146
Module Number: BR10S3L3L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 23.0581 | 7.0138 | 161.7248 | 32.8821 | 8.2082 | Hotspot formed over the cells or low fill factor or increased series resistance of module or possible potential induced degradedation.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 21.5163 | 5.7168 | 123.0046 | 31.0499 | 6.733
Difference | 5.9419 | 0.4062 | 53.2752 | 3.1179 | 0.0918
Percentage Degradation | 20.4894 | 5.4743 | 24.7792 | 8.6608 | 1.1057
Module Number: BR19S4L3M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 24.8477 | 6.8791 | 170.9295 | 33.4263 | 8.3444 | Hotspot formed over the cells or low fill factor or increased series resistance of module or possible potential induced degradedation.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 22.9191 | 5.5874 | 128.0584 | 31.2643 | 6.8277
Difference | 4.1523 | 0.5409 | 44.0705 | 2.5737 | -0.0444
Percentage Degradation | 14.3184 | 7.2898 | 20.4979 | 7.1492 | -0.5348

## Table 147
Module Number: BR19S6L2U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 22.2292 | 7.2534 | 161.2368 | 33.7475 | 8.3704 | Hotspot formed over the cells or low fill factor or increased series resistance of module or possible potential induced degradedation.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 20.581 | 5.8646 | 120.7002 | 31.6624 | 6.8156
Difference | 6.7708 | 0.1666 | 53.7632 | 2.2525 | -0.0704
Percentage Degradation | 23.3477 | 2.2455 | 25.0061 | 6.2568 | -0.8481
Module Number: BR19S7L1U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.152 | 6.8133 | 184.9942 | 34.6967 | 7.3114 | Cell performance is degraded or hotspot formed on the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.9639 | 5.5295 | 138.0373 | 32.3666 | 5.9793
Difference | 1.848 | 0.6067 | 30.0058 | 1.3033 | 0.9886
Percentage Degradation | 6.3725 | 8.1767 | 13.9562 | 3.6202 | 11.9112

## Table 148
Module Number: BR19S7L2L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.8412 | 5.9244 | 159.0182 | 34.4193 | 6.4251 | Cell performance is degraded or hotspot formed on the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.6625 | 5.4064 | 133.3361 | 32.0911 | 5.9087
Difference | 2.1588 | 1.4956 | 55.9818 | 1.5807 | 1.8749
Percentage Degradation | 7.4441 | 20.1563 | 26.0381 | 4.3908 | 22.5888
Module Number: BR19S9L4L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.5291 | 5.5278 | 152.1766 | 34.1466 | 7.7312 | Cell performance is degraded or hotspot formed on the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.5701 | 4.8432 | 123.8419 | 32.1217 | 6.8196
Difference | 1.4709 | 1.8922 | 62.8234 | 1.8534 | 0.5688
Percentage Degradation | 5.0721 | 25.5008 | 29.2202 | 5.1482 | 6.8532

## Table 149
Module Number: BR19S10L2L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 15.9346 | 4.4673 | 71.1848 | 32.9353 | 6.9648 | Cell performance is degraded or hotspot formed on the cells or low fill factor or burned cells or snail trails formed on the cells or temperature variation within cells of module.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 14.7511 | 3.8814 | 57.255 | 30.8968 | 6.0941
Difference | 13.0654 | 2.9527 | 143.8152 | 3.0647 | 1.3352
Percentage Degradation | 45.0532 | 39.7935 | 66.8908 | 8.513 | 16.0871
Module Number: BR19S10L3L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.2021 | 5.3939 | 146.725 | 34.0684 | 6.6027 | Cell performance is degraded or hotspot formed on the cells or low fill factor or snail trails formed over the cells or temperature variation within cells of module.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.2489 | 4.6585 | 117.6213 | 32.0298 | 5.7415
Difference | 1.7979 | 2.0261 | 68.275 | 1.9316 | 1.6973
Percentage Degradation | 6.1996 | 27.3062 | 31.7558 | 5.3656 | 20.4499

## Table 150
Module Number: BR19S11L3L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.8549 | 5.4381 | 146.0408 | 34.1435 | 6.3917 | Cell performance is degraded or hotspot formed on the cells or low fill factor or temperature variation within cells of module.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.9466 | 4.709 | 117.4747 | 32.1217 | 5.5722
Difference | 2.1451 | 1.9819 | 68.9592 | 1.8565 | 1.9083
Percentage Degradation | 7.3969 | 26.7096 | 32.0741 | 5.1569 | 22.9921
Module Number: BR19S11L3U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.8893 | 5.4555 | 152.1491 | 34.4561 | 6.768 | Cell performance is degraded or hotspot formed on the cells or low fill factor or temperature variation within cells of module.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.8598 | 4.7914 | 123.904 | 32.3666 | 5.9853
Difference | 1.1107 | 1.9645 | 62.8509 | 1.5439 | 1.532
Percentage Degradation | 3.83 | 26.4762 | 29.233 | 4.2886 | 18.4583

## Table 151
Module Number: BR19S12L1U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.133 | 5.3503 | 139.8198 | 34.3884 | 6.6907 | Cell performance is degraded or hotspot formed on the cells or low fill factor or temperature variation within cells of module.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.2055 | 4.6856 | 113.418 | 32.2748 | 5.9007
Difference | 2.867 | 2.0697 | 75.1802 | 1.6116 | 1.6093
Percentage Degradation | 9.886 | 27.8935 | 34.9675 | 4.4765 | 19.3891
Module Number: BR18S10L1U
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.4597 | 5.7334 | 157.4387 | 34.4274 | 6.5422 | Cell performance is degraded or hotspot formed on the cells or temperature variation within cells of module.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.3994 | 5.0608 | 128.5423 | 32.2748 | 5.816
Difference | 1.5403 | 1.6866 | 57.5613 | 1.5726 | 1.7578
Percentage Degradation | 5.3112 | 22.73 | 26.7727 | 4.3683 | 21.178

## Table 152
Module Number: BR18S5L2M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 18.908 | 5.5793 | 105.4936 | 23.3461 | 6.6865 | Cell performance is degraded or one of the end of sub-string is open circuited or cells in sub-string burned or faulty bypass diode.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 17.5267 | 5.0499 | 88.5086 | 21.9248 | 6.0941
Difference | 10.092 | 1.8407 | 109.5064 | 12.6539 | 1.6135
Percentage Degradation | 34.7999 | 24.8072 | 50.9332 | 35.1499 | 19.4403
Module Number: BR18S3L1M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 28.2664 | 5.9205 | 167.3499 | 34.2939 | 6.6059 | Cell performance is degraded or hotspot formed on the cells or temperature variation within cells of module.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 26.0875 | 4.6223 | 120.5849 | 32.0911 | 5.1953
Difference | 0.7336 | 1.4995 | 47.6501 | 1.7061 | 1.6941
Percentage Degradation | 2.5298 | 20.2094 | 22.1628 | 4.7391 | 20.4109

## Table 153
Module Number: BR18S2L3M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 26.2014 | 6.3488 | 166.348 | 33.3323 | 8.3803 | Hotspot formed on the cells or temperature variation within cells of module or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 24.2795 | 4.8744 | 118.3485 | 31.2949 | 6.479
Difference | 2.7986 | 1.0712 | 48.652 | 2.6677 | -0.0803
Percentage Degradation | 9.6504 | 14.4363 | 22.6288 | 7.4102 | -0.967
Module Number: BR18S2L2M
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 23.3704 | 7.5139 | 175.6033 | 33.7693 | 8.5103 | Increased series resistance of module or hotspot formed over the cells or low fill factor.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 21.5952 | 5.7907 | 125.0505 | 31.6317 | 6.606
Difference | 5.6296 | -0.0939 | 39.3967 | 2.2307 | -0.2103
Percentage Degradation | 19.4125 | -1.2659 | 18.3241 | 6.1963 | -2.5339

## Table 154
Module Number: BR18S2L1L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 24.4505 | 7.5837 | 185.4239 | 35.0704 | 8.7866 | Increased series resistance of module or hotspot formed over the cells or low fill factor or bubbles are formed at the backsheet of the module.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 22.3678 | 5.8956 | 131.8707 | 32.581 | 6.8861
Difference | 4.5495 | -0.1637 | 29.5761 | 0.9296 | -0.4866
Percentage Degradation | 15.688 | -2.2056 | 13.7563 | 2.5823 | -5.8621
Module Number: BR16S1L1L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.4878 | 5.3608 | 147.3576 | 34.1041 | 8.0142 | Hotspot formed over the cells or low fill factor or burned cells or cell temperature variation within the cells.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 26.2219 | 4.4949 | 117.8648 | 32.7953 | 6.7491
Difference | 1.5122 | 2.0592 | 67.6424 | 1.8959 | 0.2858
Percentage Degradation | 5.2146 | 27.7514 | 31.4616 | 5.2664 | 3.444

## Table 155
Module Number: BR15S8L3L
Value | Vmp | Imp | Pmax | Voc | Isc | Remark
Translated to STC | 27.5816 | 5.8802 | 162.1864 | 34.0571 | 7.6304 | Cell performance is degraded or hotspot formed on the cells or temperature variation within cells of module.
Rated STC | 29 | 7.42 | 215 | 36 | 8.3
Measured | 25.1949 | 4.7365 | 119.336 | 31.6011 | 6.1969
Difference | 1.4184 | 1.5398 | 52.8136 | 1.9429 | 0.6696
Percentage Degradation | 4.8909 | 20.7516 | 24.5644 | 5.397 | 8.068